




UNINTERRUPTIBLE POWER SYSTEMPRIVATE 

Part listnum "WP List 1" \l 1 - INTRODUCTION



This specification describes a continuous duty solid‑state on‑line, uninterruptible power supply (U.P.S.).  This means that AC power is converted to DC power by a rectifier/charger section, which provides power to operate the inverter and keep the batteries fully charged.  The inverter then converts the DC power back to clean, conditioned AC power.  The U.P.S. shall operate in conjunction with the existing building/plant electrical systems to provide high quality power to the critical load.  The system shall consist of a rectifier/ charger, inverter, static transfer switch, and internal maintenance bypass switch.


Part listnum "WP List 1" \l 1 - APPLICABLE STANDARDS, CODES AND REGULATIONS



Unless noted otherwise, the design, fabrication, testing, and performance of the U.P.S. system shall be in accordance with the standards and codes, where applicable, of the following agencies:


National Electrical Manufacturers Association (NEMA)


American National Standards Institute (ANSI)


National Electric Code (ANSI/NFPA 70‑1990)


Institute of Electrical and Electronic Engineers (IEEE)


National Fire Protection Association (NFPA)


Part listnum "WP List 1" \l 1 - ENVIRONMENTAL CONDITIONS



3listnum "WP List 1" \l 2 Operating Temperature



The U.P.S. shall operate at rated output without any adverse affects in an ambient temperature of 0 C to 40 C (32 F to 104 F), except batteries.

3listnum "WP List 1" \l 2 Relative Humidity


The U.P.S. shall operate at a relative humidity of 5% to 95% non‑condensing for a temperature range of 10 C to 40 C.



3listnum "WP List 1" \l 2 Operating Altitude



The U.P.S. shall operate at any altitude from sea level up to 5000 feet above sea level without derating.


Part 4 - SYSTEM DESCRIPTION



4listnum "WP List 1" \l 2 The U.P.S. system shall be of the float configuration.  During any interruption of the AC power input to the U.P.S., the battery bank shall continue to provide input DC power to the inverter with no interruption in inverter output AC power.

           

 4listnum "WP List 1" \l 2 Each U.P.S. system shall consist of the following major components:

AC Rectifier/Charger

Static Inverter

Static Transfer Switch

Manual Bypass Switch

Battery System (separate enclosure/rack)


Part 5-SYSTEM OPERATION

  

Part 6) -RECTIFIER/CHARGER


6listnum "WP List 1" \l 2 General



Incoming AC power shall be converted to regulated DC output by the rectifier/charger.  The rectifier/charger shall be a constant potential, phase‑controlled, solid‑state type with constant voltage and current control circuitry.  The components within the rectifier shall be capable of operating independently from the remaining system.


6listnum "WP List 1" \l 2 Capacity



The rectifier/charger shall have sufficient capacity to support a fully loaded inverter and to recharge the battery at the equalize condition to 90% of full capacity within 8 times the discharge time, when the input current limit is set at 125% of rated load.


6listnum "WP List 1" \l 2 Input Voltage

6listnum "WP List 1" \l 2 Input Power Factor



The input power factor shall be a minimum power factor of 0.75 at nominal input voltage, frequency, and at full‑rated load.



6listnum "WP List 1" \l 2Rectifier/Charger Output Voltage



Nominal Float Voltage: 130 VDC, adjustable +/‑5%



Nominal Equalize Voltage: 140 VDC, adjustable +/‑5%


6listnum "WP List 1" \l 2 Voltage Regulation



The charger output steady state voltage shall not change more than +/‑1% at the battery bank, at a cable length less than 10 ft., from no load to full rated load with input voltage variation of +10% to ‑10% and input frequency variation of +/‑5%.



6listnum "WP List 1" \l 2Output Ripple



The output ripple shall be less than 2% RMS when connected to a battery bank of at least four (4) times the Ah rating of the battery charger and with a cable length less than 10 ft.



6listnum "WP List 1" \l 2 Current Limit



The charger/rectifier shall be capable of supplying output current to 125% of the full rated load current at float voltage and ‑10% input voltage up to three hours.  This will not cause damage to the charger/rectifier, tripping of circuit breakers, or blown fuses.  The current limit shall be adjustable from 100% to 125% of rated output.



6listnum "WP List 1" \l 2 Locking Float Adjustment



An internal screw type adjustment shall be provided to adjust the float voltage +/‑5%.



6listnum "WP List 1" \l 2 Locking Equalize Adjustment

An internal screw type adjustment shall be provided to adjust the equalize voltage +/‑5%.

6listnum "WP List 1" \l 2Float/Equalize Timer



An internal 0‑100 Hour electronic timer shall be provided to control placing the charger into a high voltage equalize mode for a specific amount of time and then return it to its normal float mode when the time has elapsed.



6listnum "WP List 1" \l 2  Isolation



A dry type isolation transformer shall be provided for the AC input to the rectifier.


Part 7) - STATIC INVERTER


7listnum "WP List 1" \l 2 General



The static inverter shall be a ferroresonant type, which generates single phase AC power.  The inverter shall be capable of providing continuous and uninterruptible output power while operating from any DC source within the battery operating system.



The inverter bridge shall use power transistors, and IGBT's (Insulated Gate Bipolar Transistors) to generate the power input for the ferroresonant transformer.



7listnum "WP List 1" \l 2 Output Voltage



The inverter output voltage shall be single phase at a nominal voltage of 120 VAC and shall operate in accordance with this specification.



7listnum "WP List 1" \l 2 Input Voltage



The DC input voltage shall range from 105‑140 VDC while maintaining the specified output voltage.  This would be typical for a 60 cell battery bank.



7listnum "WP List 1" \l 2 Voltage Regulation



The inverter steady state output voltage regulation shall not change more than +/‑2% under any of the following conditions:

listnum "WP List 1" \l 30 to 100% and 100% to 0 load change.

listnum "WP List 1" \l 3Minimum to maximum DC bus voltage.



7listnum "WP List 1" \l 2Frequency Regulation



The free‑ running, steady state output frequency of the inverter shall not deviate more than 0.1% due to the following conditions:

listnum "WP List 1" \l 30% to 100% load

listnum "WP List 1" \l 3Minimum to maximum ambient temperature

listnum "WP List 1" \l 3Minimum to maximum DC bus voltage



7listnum "WP List 1" \l 2Frequency Control


The output frequency of the inverter shall be controlled by a crystal controlled oscillator, which can be operated as a free‑running unit or as a slave for synchronized operation with a separate AC source.  The inverter shall track the synchronized source as long as the synchronized source is 60 Hz +/‑5%.  Upon failure or excessive   frequency deviation of the reference the oscillator shall automatically revert to a free‑running unit maintaining a frequency at 60Hz +/‑0.1%.



7listnum "WP List 1" \l 2Load Power Factor



The inverter shall be capable of handling operating loads of 0.8 pf to 1.0 pf while maintaining a +/‑2% regulation.



7listnum "WP List 1" \l 2Harmonic Distortion



The inverter shall limit the total harmonic distortion of the output voltage to 5% RMS total with a 100% linear load.



7listnum "WP List 1" \l 2Crest Factor



The inverter shall be capable of supplying non‑linear loads exhibiting a crest factor of up to 3.0 at full load without additional filtering or increasing the size of the U.P.S.



7listnum "WP List 1" \l 2Slew Rate



The inverter frequency rate of change shall not exceed 1 Hz/second when synchronizing to the bypass reference.



7listnum "WP List 1" \l 2AC Transient Response



The inverter voltage transient response shall not exceed +8% to ‑12% due to a 100%‑50% or 50%‑100% step load change.  During a 100% step load the maximum deviation shall be 23% for the first half cycle.


7listnum "WP List 1" \l 2AC Transient Recovery



The output voltage following the conditions listed in 7.11 shall return to within +/‑2% of the steady state output voltage within 50 milliseconds.



7listnum "WP List 1" \l 2 Overload Capability



The inverter shall be capable of supplying loads up to 120% of the rated load for 10 minutes and loads up to 150% of the rated load for approximately 10 seconds.  The inverter shall current limit at approximately 200% without damage to the inverter.  The retransfer point shall be at 100% of rated load.



7listnum "WP List 1" \l 2 Over Temperature



During a heatsink overtemperature, the U.P.S. will automatically transfer the load to the bypass source.  Manual retransfer of the load to the inverter will be permitted if the temperature is reduced.



7listnum "WP List 1" \l 2 DC Input Transient



The DC input shall include an input filter to suppress externally generated DC transients and to impede inverter switching transients at the battery.  Filtering shall be adequate to prevent the inverter from damage when a transient of 4000 volts, having a source impedance of 40 ohms or greater and a duration of 10 microseconds is applied to the inverter input with the filter attached.


Part listnum "WP List 1" \l 1 - STATIC TRANSFER SWITCH



8listnum "WP List 1" \l 2General



The full rated static switch shall be a naturally commutated, high speed transfer device provided as an integral part of the U.P.S.  The control of the unit shall provide an automatic or manual uninterrupted transfer of the load to the bypass.



8listnum "WP List 1" \l 2 Operation



The static switch shall automatically connect the bypass source to the critical load when required and have the following features.

listnum "WP List 1" \l 3Uninterrupted Transfer ‑ The static switch shall automatically transfer and turn on the bypass
source and assume the critical load after the inverter logic senses one of the following conditions:

 listnum "WP List 1" \l 4Inverter Failure

listnum "WP List 1" \l 4Inverter Overcurrent

listnum "WP List 1" \l 4Inverter Output Over/Under Voltage (+/‑10%) >16 msec.

listnum "WP List 1" \l 4Low DC Disconnect

listnum "WP List 1" \l 4Manual Transfer

listnum "WP List 1" \l 3Uninterrupted Automatic Retransfer ‑ If the transfer control switch is set for automatic 
retransfer, the control circuit shall be capable of retransferring the critical load to the inverter 
output when the overload is removed and the inverter output is within specification.

listnum "WP List 1" \l 3Uninterrupted Manual Retransfer ‑ If the transfer control switch is set for manual retransfer, 
upon manual command the critical load shall be transferred to the inverter.

listnum "WP List 1" \l 3Transfer Lockout ‑ The transfer logic shall not allow a transfer to the bypass source if one of 
the following conditions exist:

listnum "WP List 1" \l 4Bypass source out‑of‑sync with inverter output.

listnum "WP List 1" \l 4Bypass source not available (Except for condition 8.2.1 items 1., 3., and 4.



8listnum "WP List 1" \l 2Transfer Time



The transfer time of the static switch shall be uninterruptible (zero break) under any transfer.



8listnum "WP List 1" \l 2Transfer Point



The static switch current sense transfer point shall be adjustable from 100% to 125%, factory set at 120%.



8listnum "WP List 1" \l 2Autoretransfer Defeat



An internal switch shall be provided to defeat the retransfer of the static switch after a transfer to the bypass source.  Shipment setting for the unit shall be ON (i.e. auto retransfer).


Part listnum "WP List 1" \l 1 - MANUAL BYPASS SWITCH



A manually operated mechanical bypass switch shall be provided to facilitate the U.P.S. maintenance.  In the bypass position, this switch and the static switch input breaker shall isolate the static switch from the bypass source and connect the output directly to the bypass power source.



The manual bypass switch shall be mounted in the U.P.S. enclosure to reduce total space requirements.



The manual bypass switch shall be of a "make‑before‑break" configuration to ensure absolute continuity of AC power to the critical U.P.S. loads during switch over.


Part listnum "WP List 1" \l 1 - ACCESSORIES



10listnum "WP List 1" \l 2Controls



All controls specified below shall be accessible on the front panel unless otherwise noted.

listnum "WP List 1" \l 3Inverter to Load ‑ A lighted momentary push button shall be provided to transfer the load to the 

inverter.

listnum "WP List 1" \l 3Bypass to Load ‑ A lighted momentary push button shall be provided to transfer the load to the bypass source.

listnum "WP List 1" \l 3Float ‑ A lighted momentary push button shall be provided to manually select the float mode 
on the charger.
listnum "WP List 1" \l 3Equalize ‑ A lighted momentary push button shall be provided to manually select the float 

mode on the charger.



10listnum "WP List 1" \l 2Meters



At a minimum the front panel shall be equipped with the following 3.5 inch scale analog meters (2% accuracy) for the following functions:

listnum "WP List 1" \l 3Inverter Output Voltmeter

listnum "WP List 1" \l 3AC Output Ammeter

listnum "WP List 1" \l 3Inverter Output Frequency Meter (55Hz ‑ 65Hz scale)

listnum "WP List 1" \l 3DC Output Voltmeter

listnum "WP List 1" \l 3DC Output Ammeter



Optional meters shall include:

listnum "WP List 1" \l 3AC Input Voltmeter (3 meters, 1 per phase)

listnum "WP List 1" \l 3System Output Voltmeter

listnum "WP List 1" \l 3Bypass Source Input Voltmeter

listnum "WP List 1" \l 3Battery Input Voltmeter


10listnum "WP List 1" \l 2Indicator Lights and Alarms



At a minimum the U.P.S. shall be equipped with the following equipment.  Indicators are long life LED's, front replaceable.



Alarms provide one form "C" contact (SPDT) rated for 3 Amps, 120VAC/28VDC.
listnum "WP List 1" \l 3Battery Supplying Load ‑ An indicator (Red) and alarm shall be provided to indicate when the 
battery is supplying load.  The relay shall be normally energized.

listnum "WP List 1" \l 3Bypass Source Failure ‑ An indicator (Red) and alarm shall be provided to indicate when the 
bypass source has failed.  The relay shall be normally energized.

listnum "WP List 1" \l 3Low DC Voltage ‑ An indicator (Red) and alarm shall be provided when the inverter DC input 
voltage is less than 110 VDC.  The relay shall be normally energized.

listnum "WP List 1" \l 3Fan Failure ‑ An indicator (Red) and alarm shall be provided when any fan has failed.
The relay shall be normally deenergized.

listnum "WP List 1" \l 3In Sync ‑ An indicator (Green) shall be provided when the bypass source is synchronized (as 
described in section 7.6)   with the internal oscillator of the inverter. The relay shall be normally 
energized.


Indicator Lights and Alarms Continued:

listnum "WP List 1" \l 3Low DC Disconnect ‑ An indicator (Red) and alarm shall be provided to indicate when the DC 
input breaker has tripped due to low DC disconnect.  The relay shall be normally deenergized.

listnum "WP List 1" \l 3Static Switch Transfer ‑ An alarm shall be provided when the inverter is supplying power to 
the load. The relay shall be normally energized.



10listnum "WP List 1" \l 2Optional Indicator Lights and Alarms



Indicators will be long life LED's, front replaceable.  Alarms will provide one form "C" contact (SPDT) rated for 3 Amps, 120VAC/28VDC.
listnum "WP List 1" \l 3High DC Voltage ‑ An indicator (Red) and alarm shall be provided to energize a relay when the 
rectifier output voltage is greater than 144 VDC.

listnum "WP List 1" \l 3High DC Disconnect ‑ An indicator (Red) and alarm shall be provided to indicate when the DC 
input breaker has tripped due to High DC Disconnect.  The relay shall be normally deenergized.

listnum "WP List 1" \l 3Negative to Ground ‑ An indicator (Red) and alarm shall be provided when the voltage 
between positive DC and ground exceeds approximately 65% of nominal output voltage.  This 
alarm is used in conjunction with the Positive DC Ground Detect as a voltage divider.  The relay 
shall be normally deenergized.

listnum "WP List 1" \l 3Positive to Ground ‑ An indicator (Red) and alarm shall be provided when the voltage 
between negative DC and ground exceeds approximately 65% of nominal output voltage.  This 
alarm is used in conjunction with the Negative DC Ground Detect as a voltage divider.  The relay 
shall be normally deenergized.
listnum "WP List 1" \l 3 Overtemperature ‑ An indicator (Red) and alarm shall be provided when the ambient 
temperature is excessive.  The relay shall be normally deenergized.
listnum "WP List 1" \l 3 AC Available ‑ An indicator (Green) and alarm shall be provided when AC is available to the 
charger. The relay shall be normally energized.
listnum "WP List 1" \l 3 Low AC Output ‑ An indicator (Red) and alarm shall be provided when the AC output 
voltage is less than 90% of nominal. The relay shall be normally energized.

listnum "WP List 1" \l 3High AC Output ‑ An indicator (Red) and alarm shall be provided when the AC output 
voltage is greater than 110% of nominal.  The relay shall be normally deenergized.



Optional Indicator Lights and Alarms Continued:

listnum "WP List 1" \l 3Reverse Polarity ‑ An indicator (Red) and alarm shall be provided when the battery is 
connected in reverse.  The relay shall be normally deenergized.

listnum "WP List 1" \l 3Bypass Source Available ‑ An indicator (Green) and alarm shall be provided when the bypass 
source is available.  The relay shall be normally energized.

listnum "WP List 1" \l 3Bypass Source Low Voltage ‑ An indicator (Red) and alarm shall be provided when the bypass 
source is less than 90% of nominal.  The relay shall be normally energized.

listnum "WP List 1" \l 3Bypass Source High Voltage ‑ An indicator (Red) and alarm shall be provided when the
bypass source is greater than 110% of nominal.  The relay shall be normally deenergized.

 listnum "WP List 1" \l 3AC Input Power Failure ‑ An indicator (Red) and alarm shall be provided when the AC 
input voltage has failed.  The relay shall be normally energized.

listnum "WP List 1" \l 3U.P.S. Trouble ‑ An indicator (Red) and alarm will be provided if any of the above alarm 
conditions occur. The relay shall be normally deenergized.

listnum "WP List 1" \l 3U.P.S. Trouble w/Audible Alarm ‑ An indicator (Red), alarm, audible alarm and silence 
switch will be provided if any of the above alarm conditions occur.  A switch shall also be 
provided to silence the audible alarm.  The relay shall be normally deenergized.



10listnum "WP List 1" \l 2Optional Serial Communication Port



With this option, all forms of information available on the front panel are available to the user via a 9‑pin D connector in the standard ASCII format.  Information available includes status, alarms and metering.  At any time an alarm condition occurs, it will automatically be transmitted.

listnum "WP List 1" \l 3Communications Format


Baud Rate:4800 bps

             Format:ASCII 8 data bits, one stop bit



Parity:None



Duplex:Full



Handshaking:Not required

listnum "WP List 1" \l 3Connections


The RS‑232 connections shall be:


Pin 1Power Ground


Pin 2TXD (Transmit)


Pin 3RXD (Receive)


Pin 5Signal Ground


Pin 8Clear to Send


The RS‑422 connections shall be:


Pin 1RXD


Pin 2RXD


Pin 3TXD


Pin 4TXD


Pin 5Signal Ground


Pin 8INT (Interrupt)


Pin 9INT


Part listnum "WP List 1" \l 1 - GENERAL REQUIREMENTS


11listnum "WP List 1" \l 2System Efficiency



The overall AC to AC efficiency shall be greater than 78% with the U.P.S. at full rated load and nominal input voltage.



11listnum "WP List 1" \l 2Overload Protection



The overload devices shall not be activated when the U.P.S. is started under any normal operating conditions.

listnum "WP List 1" \l 3AC Input Circuit Breaker ‑ A front access molded case breaker shall be provided for 
charger/rectifier disconnection and overload protection.  The A.I.C. rating of the breaker  shall be 
10KA minimum.

listnum "WP List 1" \l 3Bypass Circuit Breaker ‑ A front access molded case breaker shall be provided for Bypass 
disconnection and overload protection.  The A.I.C. rating of the breaker shall be 14KA 
minimum.

listnum "WP List 1" \l 3DC Input Circuit Breaker ‑ A molded case breaker shall be provided for DC input 
disconnection of both input lines and overload protection.  The A.I.C. rating of the breaker shall 
be 10KA minimum.

listnum "WP List 1" \l 3Inverter Output Circuit Breaker (optional) ‑ A molded case non‑automatic breaker shall be 
provided for Inverter output disconnection.



Overload Protection Continued

listnum "WP List 1" \l 3AC Output Circuit Breaker (optional) ‑ A molded case breaker shall be provided for AC output 
disconnection and overload protection.  The A.I.C. rating of the breaker shall be 14KA  
minimum.
 11.2.6  DC Output Circuit Breaker (optional) ‑ A molded case breaker shall be 
provided for rectifier/charger output disconnection and overload protection.  The A.I.C. rating of 
the breaker shall be 10KA minimum.
listnum "WP List 1" \l 3Semiconductor Fuses ‑ The semiconductors shall be protected from excessive overloads 
including faults and reverse currents with fast acting fuses.



11listnum "WP List 1" \l 2 Audible Noise



The audible noise generated by the unit under rated operating conditions shall not exceed 60dBA at 5 feet away from any side of the enclosure and 3 feet above ground.  The sound levels shall be measured with the unit operating at rated load, voltage and frequency.


11listnum "WP List 1" \l 2Cooling


Forced air cooling shall be provided when necessary to ensure that all components are operating 

at their specified environmental temperature.



11listnum "WP List 1" \l 2Wiring


Wiring materials and practices shall be at a minimum in accordance to UL 1015, 105 C.  All wiring shall be copper throughout the system.  PVC insulation shall be used on all insulated, internal wires.


11listnum "WP List 1" \l 2 EMI Suppression



Electromagnetic effects shall be minimized to ensure that computer systems, or other similar electronic systems, shall neither adversely affect nor be adversely affected by the U.P.S.



11listnum "WP List 1" \l 2Control Power Supply



The control logic power supply shall incorporate a parallel redundant concept with the inverter DC input and the bypass as a dual source of logic power, to insure control power at all times.


11listnum "WP List 1" \l 2Transformers



Any transformer or inductor shall be designed using copper windings for reliability and efficiency.  The insulation type shall have a temperature rating of at least 200 C (UL 1446, Class N).

11listnum "WP List 1" \l 2Nameplate Markings



The nameplate shall be located on the front inside display door and the following minimum information shall be provided on the nameplate:

listnum "WP List 1" \l 3Solid state Controls, Inc., Model # and Serial #

listnum "WP List 1" \l 3AC Input Voltage, Phase and Frequency

listnum "WP List 1" \l 3Rated AC Input Current

listnum "WP List 1" \l 3Bypass AC Input Voltage, Phase and Frequency

listnum "WP List 1" \l 3DC Input Voltage and Current

listnum "WP List 1" \l 3Rated Output Voltage, Amps, Frequency, Power Factor, KVA and KW



Part listnum "WP List 1" \l 1 - MECHANICAL SPECIFICATIONS


12listnum "WP List 1" \l 2  Enclosure



The enclosure shall be a NEMA‑1 type, free standing, with minimum 12GA framework.  Door panels shall be a minimum of 14GA steel and side panels shall be a minimum of 18GA.  The enclosure shall be mounted on channels with a 3 inch lifting base open at the front and back to facilitate moving with a fork lift and to provide an entrance area for air movement through the enclosure.

The enclosure shall be designed with blank plates on the sides and rear for installation against a 


wall. The equipment shall be designed to allow replacement or maintenance of all components from the front.

One or more hinged doors shall be provided in the front with door locks on each.  Hinged panels, 

36" and larger, shall be provided with a 2 point latching system for holding the panels securely. 


Removable covers shall be attached with machine screws.


12listnum "WP List 1" \l 2 Ventilation



Air inlets and outlets shall be protected by perforated or slotted metal guards such as to prevent the entrance of a rod having a diameter of 0.5 inches or larger.



12listnum "WP List 1" \l 2 Cable Entry


Cable entry shall be through the bottom or the top of the cabinets.



12listnum "WP List 1" \l 2Power Connections



The connections to the AC input, output or battery shall be of the stud type and shall be sized according to Article 310 of the National Electric Code.



Alarm connections shall be sized to allow connection of 12AWG wire maximum.



12listnum "WP List 1" \l 2Parts Placement



The U.P.S. shall be designed to permit front access to modules, fuses, and assemblies.  Parts, test points, and terminals shall be placed so they are accessible for circuit checking, adjustment, and maintenance without removal of any adjacent assembly or component, or pose a shock hazard.



12listnum "WP List 1" \l 2Wire Supports



Permanent wire supports shall be used, no adhesive backed wire supports shall be used.



12listnum "WP List 1" \l 2Wire Marking



All point‑to‑point wires shall be marked with a permanent marking system on both ends of each wire.



12listnum "WP List 1" \l 2Component Marking



All PCB's, indicator lights, meters, controls, semiconductors, and fuses shall be clearly marked with the component designation for ease of serviceability.



12listnum "WP List 1" \l 2Personnel Safety



The cabinet shall be constructed so that all controls are operable with the doors closed, preventing exposure to high voltage terminals.



High voltage warning labels shall be clearly visible when any of the cabinet doors are opened.



 12listnum "WP List 1" \l 2Painted Surfaces



All external painted surfaces shall be ANSI 61 Gray enamel of a minimum of 2.0 mil thickness.  It shall be smooth and even with no runs, sags, or graininess.  All internal mounting plates shall be painted white.


Part listnum "WP List 1" \l 1 - DOCUMENTATION


13listnum "WP List 1" \l 2Cabinet outline and interconnect drawings shall be dimensioned and scaled, and include the 

following information:

listnum "WP List 1" \l 3Location of any removable plates for Owner's conduit entry.

listnum "WP List 1" \l 3Location and size of all terminal blocks for Owner's connections.

listnum "WP List 1" \l 3Location and size of ventilation openings.

listnum "WP List 1" \l 3Location of cabinet grounds.

listnum "WP List 1" \l 3Block diagram including currents for customer cable sizing, breaker locations and sizes, and 
meter locations.
listnum "WP List 1" \l 3Size and weight of equipment.

listnum "WP List 1" \l 3Front panel identification chart.

listnum "WP List 1" \l 3Nominal heat loss for the specified equipment.

13listnum "WP List 1" \l 2Schematic type drawings shall include the following information:

listnum "WP List 1" \l 3System schematics shall include part designations for all components.

listnum "WP List 1" \l 3Relay contacts shall be shown in the de‑energized position.

listnum "WP List 1" \l 3Wire sizing and numbering having the same designations that will appear on the actual 
equipment.


Part listnum "WP List 1" \l 1 - PREPARATION FOR SHIPMENT


14listnum "WP List 1" \l 2Preparation for shipment shall be in accordance with the  manufacturer's standard shipping 

procedure.


14listnum "WP List 1" \l 2One complete set of instruction books and "as‑built" drawings shall be included with the 

equipment when shipped.



14listnum "WP List 1" \l 2To facilitate site access, shipment of individual cabinets, rather than complete lineups, may be necessary.

MASTER MECHANICAL
SECTION 15821 - 3
SPECIFICATION
SPRAYED COIL DEHUMIDIFIERS


REV. 12/99


