
H20.REVPRIVATE 

SELF‑CONTAINED AIR CONDITIONERS
NOTE:     FINAL DATE: APRIL, 1988.

NOTE:     REVIEW LOCAL CODE REQUIREMENTS; INCLUDE REFRIGERANT RELIEF PIPING IF REQUIRED BY CODE

NOTE:     COORDINATE THIS SECTION WITH APPROPRIATE REMOTE CONDENSER SECTION

NOTE:     REVIEW FLOOR LOADINGS.  IF PERMISSIBLE FLOOR LOAD IS EXCEEDED BY BASE DIMENSIONS OF UNITS, REVIEW NECESSARY PROVISION TO SPREAD OR CARRY LOADS AND INCLUDE APPLICABLE SPECIFICATION ITEMS

Part listnum "WP List 1" \l 1 - GENERAL


listnum "WP List 1" \l 2WORK INCLUDED



listnum "WP List 1" \l 3Work in this Section includes the providing of labor, materials, equipment and services necessary for a complete and safe installation in accordance with the contract documents and all applicable codes and authorities having jurisdiction for the following




listnum "WP List 1" \l 4Self‑contained air conditioners for operation with:

WATER





listnum "WP List 1" \l 5Remote evaporative condenser.





listnum "WP List 1" \l 5Remote air cooled condenser.





listnum "WP List 1" \l 5Remote cooling tower.

NOTE:  CHECK LOCAL CODES REGARDING USE OF CITY WATER.





listnum "WP List 1" \l 5City water.

WATER




listnum "WP List 1" \l 4Piping




listnum "WP List 1" \l 4Emergency switches.


listnum "WP List 1" \l 2RELATED WORK AND REQUIREMENTS



listnum "WP List 1" \l 3Requirements of GENERAL CONDITIONS, DIVISION NO. 1 and Section GENERAL PROVISIONS FOR HEATING, VENTILATING AND AIR CONDITIONING WORK apply to all work in this Section

NOTE:     EDIT TO SUIT PROJECT REQUIREMENTS.  INCLUDE ONLY SECTIONS DIRECTLY AFFECTING WORK OF THIS SECTION



listnum "WP List 1" \l 3Related work in the followig Sections:




listnum "WP List 1" \l 4PIPING.




listnum "WP List 1" \l 4CONDENSER WATER SYSTEM (Packaged Cooling Towers).




listnum "WP List 1" \l 4AIR COOLED CONDENSER SYSTEM.




listnum "WP List 1" \l 4EVAPORATIVE CONDENSER SYSTEM.




listnum "WP List 1" \l 4INSULATION.




listnum "WP List 1" \l 4MOTORS.




listnum "WP List 1" \l 4VIBRATION ISOLATION.




listnum "WP List 1" \l 4‑‑‑‑‑.


listnum "WP List 1" \l 2REFERENCE STANDARDS



listnum "WP List 1" \l 3Published Specifications' standards, tests, or recommended methods of trade, industry or governmental organizations apply to work in this Section



listnum "WP List 1" \l 3Comply with all applicable national, state and local codes and refer to Section GENERAL PROVISIONS FOR HEATING, VENTILATING AND AIR CONDITIONING WORK for additional Reference Standards


listnum "WP List 1" \l 2QUALITY ASSURANCE



listnum "WP List 1" \l 3Refer to Section GENERAL PROVISIONS FOR HEATING, VENTILATING AND AIR CONDITIONING WORK for Guarantee and other Quality Assurance requirements


listnum "WP List 1" \l 2SUBMITTALS



listnum "WP List 1" \l 3Submit shop drawings, catalog cuts and wiring diagrams for self‑contained air conditioners

Part listnum "WP List 1" \l 1 - PRODUCTS


listnum "WP List 1" \l 2BASE BID MANUFACTURERS:  Carrier Air Conditioning Co., Trane Co. and York Corp


listnum "WP List 1" \l 2PIPING AND FITTINGS



listnum "WP List 1" \l 3Refer to Section "PIPING" for condensate drain, refrigerant and cold water piping



listnum "WP List 1" \l 3Fittings:  Threaded galvanized cast iron, drainage type fitting for condensate drain.  Soldered wrought copper type for refrigerant piping


listnum "WP List 1" \l 2SELF‑CONTAINED AIR CONDITIONERS



listnum "WP List 1" \l 3Air conditioner shall be factory assembled, tested, dehydrated, lubricated oil charge and refrigerant charge in accordance with ASME Code and UL approved with independent refrigerant circuit for each compressor and minimum capacities as noted



listnum "WP List 1" \l 3Compressors:  Hermetic type, direct driven 1750 rpm with unloaded starting, vibration isolators, crankcase heater, hot gas muffler reversible rotating oil pump, and capacity control

STEP




listnum "WP List 1" \l 4Compressors in sequence.




listnum "WP List 1" \l 4Step unloading.

STEP



listnum "WP List 1" \l 3Fan assembly:  Centrifugal fan with motor and variable pitch pulley up to 25 hp or fixed pitch pulley above 25 hp




listnum "WP List 1" \l 4Supply replacement fixed pitch pulleys as required to balance system




listnum "WP List 1" \l 4Supply one set of replacement pulleys and belts.




listnum "WP List 1" \l 4Matched belts shall be rated at 150 percent rated hp.




listnum "WP List 1" \l 4Belt guard if belts are exposed and bearing lubrication system



listnum "WP List 1" \l 3Cooling coils:  Copper tubing with aluminum fins and galvanized tube sheets with number of circuits to match compressors.



listnum "WP List 1" \l 3Insulated Drain Pan.



listnum "WP List 1" \l 3Heating Coils:  Copper tubing with aluminum fins.

TYPE




listnum "WP List 1" \l 4Steam distributing tube type.




listnum "WP List 1" \l 4Hot water type.

TYPE



listnum "WP List 1" \l 3Filters:  Refer to Section "AIR HANDLING SYSTEM EQUIPMENT".  Filter box shall be suitable for

ARRANG




listnum "WP List 1" \l 4V‑bank arrangement.




listnum "WP List 1" \l 4Flat arrangement.

ARRANG



listnum "WP List 1" \l 3Insulate casings and pipe.



listnum "WP List 1" \l 3Condenser:

NOTE:     IF WATER WORKING PRESSURE EXCEEDS 125 PSIG, CHECK AVAILABILITY OF SUITABLE CONDENSER WITH MANUFACTURER




listnum "WP List 1" \l 4Multi‑pass shell‑and‑coil or multi‑pass shell‑and‑tube with copper coils or tubes, pressure relief valve, liquid line shutoff valve and refrigerant charging valved connection




listnum "WP List 1" \l 4Water side working pressure shall be minimum 125 psig

PIPED




listnum "WP List 1" \l 4Piped for cooling tower water.

NOTE:     FOR CITY WATER COOLED UNITS.




listnum "WP List 1" \l 4Piped for city water.

PIPED



listnum "WP List 1" \l 3Water regulating valves.



listnum "WP List 1" \l 3Refrigeration accessories:  For each circuit shall follows:




listnum "WP List 1" \l 4Combination filter and drier in liquid line with two replaceable cartridges, similar to Sporlan Catchall Replaceable Core Type




listnum "WP List 1" \l 4Combination sight‑glass and moisture indicator in liquid line, similar to Sporlan See‑All




listnum "WP List 1" \l 4Thermostatic expansion valves with external equalizer, superheat adjustment, and capillary and bulb charge, similar to Sporlan Valve Co



listnum "WP List 1" \l 3Control cabinet, factory mounted and prewired shall be as follows




listnum "WP List 1" \l 4Combination fused disconnect switch and magnetic starter type controller for each motor




listnum "WP List 1" \l 4Refrigerant dual pressure switches with manual reset on high pressure cutout




listnum "WP List 1" \l 4"OFF‑FAN‑COOL" switch.




listnum "WP List 1" \l 4Terminal block.




listnum "WP List 1" \l 4Compressors interlocked with fan to prevent operation unless fan is operating




listnum "WP List 1" \l 4Time delay relay to prevent compressor short cycling.



listnum "WP List 1" \l 3Compressor motors shall be high starting torque type and conditioner shall be similar to Carrier Air Conditioning Co. Model ‑‑‑‑‑

NOTE:     COORDINATE WITH ELECTRICAL DEPARTMENT.


listnum "WP List 1" \l 2REFRIGERATION EMERGENCY SWITCH



listnum "WP List 1" \l 3Provide break‑glass type, similar to Acme Fire Alarm Co. 390 Series, to stop unit and to start room exhaust fan if it is not operating

Part listnum "WP List 1" \l 1 - EXECUTION


listnum "WP List 1" \l 2INSTALLATION



listnum "WP List 1" \l 3Piping:




listnum "WP List 1" \l 4Condensate drain:  From drain pan to floor drain shall be minimum 1 1/4 inch pipe with trap seal to prevent air leakage. Minimum seal shall be equal to static pressure in drain pan




listnum "WP List 1" \l 4Refrigerant:  Relief piping from unit to atmosphere and refrigerant piping between unit and remote condenser


listnum "WP List 1" \l 2FIELD QUALITY CONTROL



listnum "WP List 1" \l 3Refrigerant piping:  Test in accordance with requirements of authorities having jurisdiction 

