Section 15171

MOTOR CONTROLLERS

Part 1. GENERAL

1.1 WORK INCLUDED

A. Furnish equipment and services necessary for a complete and safe installation in accordance with the contract documents and all applicable codes and authorities having jurisdictions for the following

1. Motor controllers for:

a. Chillers.

b. Variable frequency drives.

c. Packaged equipment.

d. Others as specified elsewhere.

e. (Others).

B. Locations of motor controllers are diagrammatic; coordinate with motor and space conditions

C. On nameplates, indicate horsepower, voltage and equipment controlled including system, equipment number and area served

1.2 RELATED WORK AND REQUIREMENTS

A. Requirements of GENERAL CONDITIONS, DIVISION No. 1 and Section GENERAL PROVISIONS FOR ELECTRICAL WORK apply to all work in this Section

NOTE:   EDIT TO SUIT PROJECT REQUIREMENTS.  INCLUDE ONLY SECTIONS DIRECTLY AFFECTING WORK OF THIS SECTION

B. Related work in the following Sections:

1. WIRE AND CABLE.

2. LOW VOLTAGE DISTRIBUTION EQUIPMENT.

3. MOTOR CONTROL CENTERS.

4. POWER, CONTROL AND ALARM WIRING SYSTEMS.

5. GROUNDING SYSTEM.

6. -----.

1.3 REFERENCE STANDARDS

A. Published Specifications' standards, tests or recommended methods of trade, industry or governmental organizations apply to work in this Section

B. Comply with all applicable national, state and local codes and refer to Section GENERAL PROVISIONS FOR ELECTRICAL WORK for additional Reference Standards

1.4 QUALITY ASSURANCE

A. The installation shall be in accordance with NEMA, IEEE and ANSI Standards

B. Refer to GENERAL PROVISIONS-MECHANICAL.

C. Refer to Section GENERAL PROVISIONS-ELECTRICAL for Guarantee and other Quality Assurance requirements

1.5 SUBMITTALS

A. Submit product data and diagrams for the following items per the provisions of Division 1 and this Division’s General Provisions:

1. Product data:  catalog cuts showing dimensions and ratings.  Submit guaranteed minimum efficiencies of motors with driven equipment submittal.

2. Diagrams:  wiring diagrams with electrical characteristics and connection requirements for each motor controller supplied under this section and requiring field wiring.

Part 2. PRODUCTS

2.1 MANUFACTURERS

A. Motor controllers:

1. Allen-Bradley.

2. Cutler-Hammer.

3. General Electric.

4. Square D.

5. Westinghouse.

2.2 MOTOR CONTROLLERS

A. Individually Mounted Controllers:

1. Type:  All controllers full voltage non-reversing type unless otherwise noted.

2. Enclosures:  NEMA general purpose, except as noted.

3. Components:

a. Terminals:  Copper for copper conductor and aluminum for aluminum conductors.

b. Overload protection:  In each phase leg with reset in enclosure.  Sizing of overload protection shall be as per motor manufacturer's recommendation for the particular motor.

c. Pilot lights:

1) 6 V incandescent lamps.

2) Candelabra base receptacle with transformer for lamps.

3) Provide positive indication for motors with local disconnect switches.

d. For fused switch combination controllers.

1) Fuses shall be similar to Bussmann:

a) Fusetron

b) Lo-Peak

c) Hi-Cap

e. Switches:  Horsepower rated, external padlocking type.

f. Auxiliary relays:

1) To supplement auxiliary contact in controllers:  Minimum 10 W coil and 2 normally open and 2 normally closed contacts.

2) With step-up auxiliary transformer where required, for remote control operation over 400 ft. from controllers.

3) For automatically operated motors over 40 hp with adjustable time delay set to prevent restarts until motor has come to a complete stop.

4) For automatically operated motors over --- HP on emergency supply with adjustable time delay relay to delay restart on normal power failure.

4. Manual type:

a. Toggle switches with overload protection.

b. Manual automatic control with run/auto selector switch.

5. Magnetic type:

a. Coil:  Minimum 10 W, 110 to 125 V operating.

b. Contacts:  Main line and minimum 2 normally open and 2 normally 10 Amp auxiliary.

c. Control transformer:  For motors over 120 V to step down control voltage to 120 Volts; of required capacity with fuse and ground connection on low voltage side.

d. Manual control:  Momentary contact push buttons, pilot light and low voltage protection.

6. Manual-automatic control:  Provide HOA selector switch, pilot light and low voltage release as required.  Wire safety controls common to manual and automatic control.

B. Controller Type:  Equal to Cutler-Hammer, of catalog numbers specified, modified as noted.  Coordinate controller and auxiliaries with motors supplied.

1. Manual type:

a. Single speed:

1) Two pole manual type with pilot light and overload protection.

2) Run/auto selector switch for automatic operation.

3) Catalog No. 9101.

b. Two speed:

1) FAST-SLOW-OFF selector switch with overload protection for each speed and two pilot lights.  Automatic time delay between fast and slow selections.

2) Run/auto selector switch for automatic operation.

3) Catalog No. 9106.

2. Magnetic type:

a. For single motors:

1) Full voltage combination non-reversing magnetic starter, with unfused disconnect switch, reset button, pilot lights and overload protection.

2) START-STOP pushbuttons, or HOA selector switch, as required.

3) Catalog No. A30.

b. For group wired motors:

1) Full voltage combination non-reversing magnetic starter, with fused disconnect switch, reset button, pilot lights and overload protection for:                    

2) START-STOP pushbuttons, or HOA selector switch, as required.

3) Catalog No. A30.

c. Two speed type:

1) Full voltage combination non-reversing magnetic starter, with unfused disconnect switch, reset button, red, green and amber indicating lights and overload protection for each speed.  Automatic time delay between fast and slow selections.

2) Two speed, one winding.

3) Two speed, two windings.

4) FAST-SLOW-STOP pushbuttons.

5) Decelerating relays for automatic high to low speed operation.

6) Time delay relays for automatic reversing.

7) Catalog No. A700 as required by motor winding.

3. Reduced inrush type:

a. Closed transition, star-delta type.

1) Combination unfused disconnect switch and magnetic starter with reset button, pilot lights and overload protection.

2) START-STOP pushbutton, or HOA selector switch, as required.

3) Cat. No. A490.

b. Part winding type.

1) Combination unfused disconnect switch and magnetic starter with reset button, pilot lights and overload protection.

2) START-STOP pushbutton, or HOA selector switch, as required.

3) Catalog No. A460.

c. Autotransformer, closed transition type.

1) Combination unfused disconnect switch and magnetic starter with reset button, pilot lights and overload protection.

2)      steps,      % taps.

3) START-STOP pushbutton, or HOA selector switch, as required.

4) Catalog No. A400.

4. Pushbutton station with:

a. START-STOP oiltight pushbutton with pilots light and lockout provision.

b. Catalog No. 10250T.

5. Hand-Off-Auto station with:

a. Oiltight HOA selector switch, pilot lights and lockout provision.

b. Catalog No. 10250T.

6. Fuses:  Specified in DIVISION 16 - ELECTRICAL.

7. Elapsed time meter for each motor.

8. For duplex units:

a. 4PDT transfer switch.

b. Automatic electric alternator.

Part 3. EXECUTION

3.1 INSTALLATION

A. Determine exact controller locations.

B. Mounting shall be:

1. On walls, columns or angle iron framework as indicated.

2. On concrete foundations over floor channels.

3. Provide angle iron framework and floor channels.

C. Where packaged equipment is provided with factory mounted pre-wired control panels and motors, (panels containing starting and control equipment) a single point power connection will be made under Division 16.

D. Where other motor controllers and/or control panels, alarm switches, or control devices are supplied loose for packaged equipment, they will be installed as specified in Division 16.  When there are air, water or other fluid connections, they shall be mounted as specified in this Division.  

E. Drawings indicate engineers understanding of system electrical requirement.  Systems supplied with requirements that differ from that will be supplied at no additional cost to the Owner.  Power connections to the motor controller/panel and from the motor controller/panel to the motor(s) will be provided as specified in Division 16.

F. Motor controllers and/or control panels for other equipment supplied under this section, will be installed as specified in Division 16, with power wiring connection as described above.

G. Control wiring, air, water or other fluid connections shall be provided. 

3.2 TESTING

A. Measure insulation resistance of each starter section phase to phase and phase to ground with the starter contacts closed and the protective device open

B. Measure insulation resistance of each control circuit with respect to ground

C. Test motor overload units by injecting primary current through overload unit and monitoring trip time

D. Perform operational tests by initiating control devices to affect proper operation

END OF SECTION

Company

Motor Controllers

Project Name
15171-1
October 21, 2000

