ITEM 02660.860YZZ M – PAD MOUNTED DISTRIBUTION TRANSFORMERS

Page 1 of 3 04/05/1

DESCRIPTION:

This work shall consist of furnishing and installing a Pad Mounted Distribution Transformer in accordance

with the plans, specifications and as directed by the Engineer.

MATERIALS:

Transformer: As manufactured by General Electric, Siemens/ITE, Square D,

Westinghouse or an approved equal. The transformer shall be UL listed

and labeled, and meet all applicable NEMA and IEEE standards.

Enclosure: Outdoor rainproof code gauge steel housing with hinged removable flip-top

hood. Phophatized and finished with corrosion inhibiting undercoat and

ANSI-61 gray baked enamel. Transformers shall be suitable for mounting

on a concrete foundation, meeting the requirements of Section 555, with a

NEMA 3R enclosure in accordance with NEMA standards. Include

provision for locking and overall tamper resistant design.

Core and Coil: Constructed of continuous copper or aluminum windings and high grade

non-aging, grain oriented silicon steel core laminations having high

magnetic permeabilities and low hysteresis and eddy current losses.

Temperature Rise: Winding temperature rise by resistance limited to 115 degrees C for

transformer sizes below 30 KVA; and 150 degrees C for transformer sizes

30 KVA and larger, referenced to 40 degrees C ambient temperature. Hot

spot temperature shall not exceed 30 degrees C above winding temperature

rise rating. Case temperature shall not exceed 35 degrees C above 40

degrees C ambient temperature.

Insulation System: Minimum 185 degrees C temperature class for transformer sizes below 30

KVA; and minimum 220 degrees C temperature class for transformer sizes

30 KVA and larger.

Primary Voltage Connection: Radial feed universal high voltage bushing well and load break bushing.

Secondary Voltage Connection: NEMA 4-hole terminal pad and grounding.

Primary Fuse:

Taps: Two 5% FCBN taps for transformer sizes below 30 KVA; and two 2-

1/2% FCAN and four 2-1/2% FCBN taps for transformer sizes 30 KVA

and larger; referenced to nameplate voltage.

Switch: Externally operated load break switch.

Noise Levels: Less than ANSI standards.

ITEM 02660.860YZZ M – PAD MOUNTED DISTRIBUTION TRANSFORMERS

Page 2 of 3 04/05/1

Ratings: KVA rating, voltages, phases and configurations is indicated.

Minimum impedance: 4.5%

BIL rating: 95 kV.

Labels: NEMA safety labels.

Test Data: Losses at 0, 25, 50, 75, 100% rated load; percent regulation at 0.8 and 1.0

power factor; % X and % R values; maximum sound level of transformer

in enclosure; and maximum hot spot and average temperature rise over 40

degrees C ambient.

BASIS OF ACCEPTANCE:

Acceptance of the Pad Mounted Distribution Transformer will be based on manufacturer’s certification of

compliance with these specification requirements.

CONSTRUCTION DETAILS:

Shop Drawings: Indicating ratings, dimensions and features for each transformer and all

accessories, including recommended pad dimensions, used on the project,

shall be submitted to the engineer for approval. The contractor is not to

order materials until approval is obtained.

Mounting: Install transformer with cleats for anchoring. Install neoprene pad to

transformer seal. Standard specification 705-08 Preformed Closed Cell

Foam Material.

Foundation: All transformers shall include a foundation in accordance with NEMA

standards, contract drawings, and manufacturers recommended pad.

Transformer terminals to face the street.

Clearance: A minimum of 3 meters of clear working distance shall be maintained.

Ground: Shall be installed as indicated on plans or as required by NEC.

Bollards: Provide steel fender posts for transformers in greenspace.

Fusing: Provide 10% spare.

Taps: Set transformer taps as required to achieve rated secondary voltage.

Testing: The testing requirements of IEEE C57.12.90 shall apply. I.A.W.

Manufacturer’s written instruments.

METHOD OF MEASUREMENT:

The work will be measured as the number of transformers installed.

ITEM 02660.860YZZ M – PAD MOUNTED DISTRIBUTION TRANSFORMERS

Page 3 of 3 04/05/1

BASIS OF PAYMENT:

The unit price bid for each transformer shall include the cost of furnishing and installing with electrical

connections, foundation, enclosures, field adjustments and all labor, materials, and equipment to complete

the work.

PAYMENT WILL BE MADE UNDER:

Item No. 02660.860YZZ

Pad Mounted Distribution Transformer

Y = Voltage Ratings

1 – (7600 – 240/480), 2 – (7600 – 120/240)

3 – (7600 GY – 277/480), 4 – (7600 GY – 120/208)

ZZ = Rating in KVA.

01 10 Single Phase

02 25 Single Phase

03 37.5 Single Phase

04 50 Single Phase

05 30 Three Phase

06 75 Three Phase

07 112.5 Three Phase

08 150 Three Phase
