WM Group Engineers, P.C.


SECTION 15600

PREFABRICATED UNDERGROUND PIPING
Part 1 -  GENERAL

1.01 DESCRIPTION OF WORK

A. For General Mechanical Requirements, see Section 15010.

B. Prefabricated underground piping shall be installed in strict accordance with the manufacturer's recommendations.

C. Provide and install complete and operable distribution systems as required and specified herein, including all components and accessories.

D. The entire chilled water, steam and condensate distribution system and all components and accessories shall be provided by the same Manufacturer.

1.02 EXAMINATION OF SITE

A. After the distribution system is completely surveyed by the certified surveyor and staked out, the Contractor shall notify the Engineer for examination.

B. The Contractor, Engineer and Owner will review the routing for deviation, if any, from the Contract Drawings.

C. No materials shall be ordered for the distribution system until the Contractor has received written approval from the Engineer on the distribution routing and has approved shop drawings of both plans and profiles.  Profiles shall be made as indicated on the contract drawings.

1.03 FACTORY SHOP DRAWING SUBMITTALS

A. Factory shop drawings shall include all manufacturers’ engineering calculations and stress analysis throughout the entire distribution system.  Shop drawings shall also be provided with all locations of cold springing, factory welds, field welds, dimensions, elbows, anchors, etc.  Factory product data shall also be provided.  Submit shop drawings of chilled water and steam distribution system as a single composite and complete package.  Shop drawings shall be based upon the data found during the test pit excavations.  No shop drawing will be accepted until the test pit excavations have been performed and incorporated.  Shop drawings shall include all necessary profiles indicating all test pit results.  Profiles shall be similar in layout as those in the contract documents.  Submit stress analysis and heat loss calculations.  Shop drawing submittals shall be fully coordinated with all of the work of all other disciplines.

1.04 SUBSTITUTIONS

A. All of the named manufacturers are acceptable.  Any other manufacturer must prove equality.  A substituted manufacturer must request the Engineer’s approval in writing. 

Part 2 -  PRODUCTS

2.01 GENERAL

A. General Requirements for Underground Piping:

1. Prior to any test pit or test exploratory, a survey layout showing the manholes and piping path shall be made and field staked for review by the Engineer.  The survey layout shall be submitted to the Engineer for record.

2. Where any existing utility intersects in plan view with the new underground system which is not noted as being test pitted shall be verified by test pit excavation for location and invert elevation.  Where existing utility depths are not shown in elevation on the profiles, the Contractor for bidding purposes shall assume the following depths for utility test pit excavations:

EXISTING UTILITY                          DEPTH BELOW GRADE
Sanitary                                       
7 feet

Storm Water
6 feet

Water
4 feet

Electric
4 feet

Telephone
4 feet

Steam and/or Condensate System
10 feet

Any Other System
5 feet

3. Where new pre-cast manholes are indicated on the drawings, the Contractor shall excavate to make certain that the manhole may be installed without any interference of known or unknown existing utilities or other types of obstacles.  The words "Site Utility" shall be cast on all manhole covers.  The Contractor shall also survey for any additional utilities not shown on the contract drawings by removing existing manhole covers in the proximity of the path of the new underground system.

4. The Contractor shall submit shop drawings (plans and profiles) based on field conditions resulting from the test pit excavations, test exploratories, and verification of new manhole locations.  This shall be done before any new piping or manholes are fabricated.

5. All test pits shall be dug in such a manner as to avoid damage to existing utilities.  Any existing utility damage shall be the responsibility of the Contractor.

6. Test pits shall be backfilled immediately after utilities have been located and recorded.  Provide temporary cold patch in streets and sidewalks.

7. All utility outages of any type shall be coordinated fourteen (14) days in advance with the University.  Outages may have to be scheduled nights, weekends, or holidays.

8. Test pits, when locating existing utilities, shall be 2'-0" wide by 6'-0" in length along the axis of the new underground line.
B. All piping shall be tested at one and one-half times the design pressure.  Test all pipe welds in accordance with specifications.  Concealed pipe welds in prefabricated conduit fittings shall be factory tested the same as specified for field welds prior to assembly.  Piping shall be suitably spaced and supported in conduit by specially designed round insulating support-guides and shall permit the pipe to expand and/or contract freely without stress or wear on the pipe or insulation as well as provide for drainage and free air circulation.
C. Contractor shall provide one week notification to the Owner prior to all testing so that an Owner's representative may be present.

D. A Manufacturer's Field Service Instructor is to be present during critical periods of installation and all testing of the conduit system.  Critical periods are defined as:  product loading and unloading; coating patch work; all field joint closure work; concrete anchor pouring; inspection of all trenches before installing conduit; and inspection of backfill.  Instructor should be factory trained and technically qualified with at least 10 years of experience to determine whether or not the installation is being made in accordance with the manufacturer's recommendation.  On completion of the installation, the Contractor shall deliver to the Owner a certificate from the Manufacturer stating that the installation has been made in accordance with the Manufacturer's recommendations.
E. Backfill:  A 12" layer of sand shall be placed and tamped in the trench to provide a uniform bedding for the pipe.  Immediately after installation in the ditch, a partial backfill shall be made to the middle of each unit leaving the joints exposed for inspection.  The entire trench width shall be evenly backfilled with a similar material as the bedding in 6 inch compacted layers to a minimum height of 6 to 12 inches above the top of the insulated piping system.  The remaining trench shall be evenly and continuously backfilled in uniform layers with suitable excavated soil with no stones, frozen earth, or foreign matter over 2" in diameter.  Do not use tracked or wheeled vehicles for tamping.
2.02 PREFABRICATED UNDERGROUND CHILLED WATER CONDUIT SYSTEM

A. General:  All underground chilled water conduit system lines shall be the “PolyTherm” type with standard weight black steel service pipe, as manufactured by Perma-Pipe or as approved equal manufactured by Insul-Tek, or Urecon.  The pipe shall be insulated with polyurethane foam and enclosed in an outer jacket of FRP or PVC.  All sections shall be prefabricated in 20 foot lengths, with end seals, provided on both ends of each piece.  Factory-trained field technical assistance (with at least 10 years experience) shall be provided for the critical periods of installation; i.e., product loading and unloading, field joint closure work; concrete anchor pouring, inspection of trench before installing pipe, inspection of backfill and testing.

B. Service Piping:  Internal piping shall be standard weight black steel, ASTM A53, seamless, Grade B.  All joints shall be butt welded.  Where possible, straight sections shall be supplied in 20 or 40 foot random lengths with 6 to 8 inches of piping exposed at each end for field joint fabrication.

C. Accessories:  Fittings, such as elbows and tees, shall be compatible with the service piping and shipped loose by the system supplier.  End seals, gland seals and anchors shall be designed and factory fabricated to prevent the ingress of moisture into the system.

D. Service pipe insulation shall be as hereinafter specified.
E. Protective Jacket:  The protective jacket shall be filament wound, polyester resin/fiberglass reinforcement composite, directly applied on the insulating foam, or seamless Polyvinyl Chloride (PVC), Type 1, Grade 1 conforming to ASTM D1784.  The minimum thickness for FRP jacket shall be as follows; for jacket diameter up to 15.5 inches - thickness = 0.055 inches; for jacket diameter between 15.6 and 24.5 inches - thickness = 0.085 inches.  The minimum thickness for PVC jacket shall be as follows; for jacket diameter up to 5 inches - thickness = 0.060 inches; for 6 inch jacket diameter - thickness = 0.070 inches; for jacket diameter greater than 6 inch - thickness = 1% of diameter.  All fittings of the insulated piping system shall be prefabricated and jacketed in a polyester resin/fiberglass reinforcement composite or seamless polyvinyl chloride (PVC), Type 1, Grade 1, conforming to ASTM D1784.

F. End Seals:  Both ends of each 20-foot length of pipe shall have end seals to prevent the ingress of moisture into the foam insulation.  Factory-made end seals for FRP jacket shall consist of fiberglass jacket being wound down over the ends of the insulation to the service pipe.  Factory made end seals for PVC jacket and end seals at field cuts for both jackets shall be heat shrink type, and shall adhere to both the jacket and the service pipe.

2.03 PREFABRICATED STEAM AND CONDENSATE CONDUIT SYSTEM

A. Prefabricated conduit system shall be Perma-Pipe “Multi-Therm 500” System, or as approved equal of “Insul-Tek".  All systems shall be provided with 1-inch air space between pipe insulation and inside conduit wall.  The following system descriptions are based on Perma-Pipe “Multi-Therm 500”.  Test for holidays in outer coating of metallic conduit and manholes in accordance with NACE Standard RP02.

B. Conduit System:  Conduit shall be 10 gauge smooth wall steel, which, in turn, is insulated with 1 inch of spray applied polyurethane foam, having a nominal 2 pound per cubic foot density, and finished with a fiberglass jacket.  The polyurethane foam shall meet ASTM C591 and have the minimum characteristics of 0.14 K-factor, and a closed cell content of 90 to 95%.  The non-metallic outer jacket shall be fiberglass (FRP) and shall be filament wound directly onto the polyurethane foam insulation.  All straight lengths and fittings shall be factory jacketed.  Conduit closures shall be furnished with the conduit at a ratio of one closure for each fabricated item or length.  Closures shall consist of 10 gauge steel of gauge thickness compatible with mating conduit, suitably rust-proofed and in cylindrical form with a single horizontal split and shall be field welded over adjacent units.  After test all exposed closures shall be covered in the field with a shrink sleeve.  All materials and insulation required for complete field closure shall be furnished with the conduit.
C. All piping in conduit shall be as hereinafter specified for the service required.
D. All piping in conduit shall be insulated as hereinafter specified.

E. Prefabricated ells, loops and tees shall be furnished and installed where shown and shall consist of pipe, insulation, and conduit conforming to the same specification as hereinbefore specified.  Expansion loops shall be of proper design in accordance with stress limits indicated by The Code for Pressure Piping, ANSI B31.1.  Loop piping shall be installed in a conduit suitably sized to handle required pipe movement.

F. Terminal ends of conduits inside manholes, pits, tunnels, or buildings shall be equipped with end seals consisting of a steel bulk head plate welded to the pipe and conduit.  Where there is no anchor within five feet of a terminal end, conduits shall be equipped with gland seals consisting of a packed stuffing box and gland follower mounted on a steel plate welded to end of conduit.  End seals or gland seals shall be equipped with drain and vent openings located diametrically opposite on the vertical center line of the mounting plate and shall be shipped to the job site with plugs in place.  Terminate all conduits 6" beyond the inside face of manhole or building walls or floors to protect any exposed piping insulation from damp-wall condensation.

G. To provide an effective moisture barrier, conduits shall be equipped with leakplates in manhole walls, but only when there is an anchor plate within 5 feet outside the wall.  Leakplates shall consist of a steel plate flange 4" larger in outside diameter than the conduit, welded to the conduit only and located in the wall or floor approximately 10" from the end of the conduit.  Where anchors are not located within 5 feet of the wall, provide water-tight modular ("Link Seal" by Thunder-line) wall sleeves.  Also, provide a waterproof membrane at all wall and floor penetrations.

H. Prefabricated plate anchors shall be furnished and installed where shown and shall consist of a steel plate welded to pipe and conduit.  The steel plate shall be 3/8" thick for 6-5/8" to 10-3/4" conduit, 1/2" thick for 12" to 22" conduit.  A concrete block shall be cast over the plate and conduit and shall be large enough for firm anchorage into undisturbed trench sidewalls and/or bottom.  The concrete block shall be at least 30" in length and extend a minimum of 9" beyond the top and bottom of the anchor plate.

I. All field welds at conduit closures shall be tested for leaks before applying shrink sleeve.  During test, all field welds shall be checked with soap suds and rewelded if necessary until air tight at 15 psig pressure.  The Contractor shall furnish all necessary equipment and labor to perform the air test, including air compressor, gauges, conduit caps, temporary pipe and connections, etc., and complete the test to the satisfaction of the Engineer.

2.04 BURIED CAUTION TAPE 

A. Provide caution tape 12" directly above buried preinsulated piping systems and conduit systems.  Tape shall be 6" wide, black in color with "STEAM", “CHILLED WATER” or “PCR”, as applicable, labeled on the tape in white lettering.

2.05 MANHOLES

A. Manholes shall be pre-cast concrete type and constructed as designed and specified under another division.

B. Work shall include but not be limited to all structural work, excavation, sheeting, backfilling, concrete work, waterproofing, reinforcement, brick work, dewatering, and manhole frames and covers.

C. The words "Site Utility” shall be cast on all manhole covers.  Round frames and covers shall be Neenah Foundry Co., or approved equal.  Provide Type 1915 manhole frame with solid Type "L" lid, Type "F" concealed watertight pickholes, frame with neoprene gasket, and counter-sunk stainless steel blue devil security bolts.  Size of manhole covers shall be as indicated on the contract drawings.

2.06 LADDERS

A. Provide each manhole with 18 inch wide properly supported, galvanized structural steel ladders designed in accordance with OSHA regulations with 1 5/8 inch diameter side rails and 13 gauge 1 5/8 inch wide x 1 1/4 inch deep perforated treads installed 12 inches on center.

B. Provide each ladder with Bilco LadderUP safety post extension.

2.07 INSULATION

A. Chilled water pipe insulation:  Service pipe insulation shall be spray applied or poured in place polyurethane foam with the following minimum properties: Two (2) pounds per cubic foot density, 90-95% closed cell content, initial thermal conductivity K of 0.13. The foam shall completely fill the space between the carrier pipe and jacket.  Minimum insulation thickness for all size piping shall be 2", or as indicated on project drawings.
B. Steam pipe insulation within conduit system shall be cellular glass in accordance with ASTM C552 with minimum 2" thickness, or as indicated on project drawings.

C. Pumped condensate return pipe insulation within conduit system shall be cellular glass in accordance with ASTM C552 with minimum 1 1/2" thickness, or as indicated on project drawings.

2.08 PIPING

A. Chilled water piping shall be Standard Weight black steel ASTM A53, seamless Grade B, butt-welded at joints.
B. Steam carrier piping shall be Standard Weight black steel ASTM A53, seamless, Grade B, butt-welded at joints.

C. Pumped condensate return carrier piping shall be Schedule 80, seamless, black steel, ASTM A53, Grade B, butt-welded at joints for piping 2-1/2" and larger, socket welded joints for piping 2" and smaller.

D. Manufacturer shall submit certificates from the foundry stating piping and conduit is in accordance with specifications.

Part 3 -  EXECUTION

3.01 PENETRATIONS AT EXISTING BUILDINGS AND MANHOLES

A. After the piping sleeves and/or conduits have been placed through existing walls or floors, the remaining voids shall be filled with modular type seals.  Provide "Link Seal" by Thunderline, or approved equal.  The wall or floor should be waterproofed with a waterproofing material that is compatible with the existing waterproofing material and should cover all exposed areas to insure a sealed surface.

3.02 INITIAL BACKFILL

A. Provide 12 inches of sand bedding completely around preinsulated system and conduit system before providing final backfill.

3.03 M-SCOPING

A. After the underground routings have been staked out, the Contractor shall M-Scope, (or by means of another approved method), the entire routing for existing underground utilities not indicated on the contract drawings.  Where additional underground utilities are detected, additional test pits will be required in accordance with Section 01026 - "UNIT PRICES".

3.04 WELDING

A. All welds, both in the factory and in the field, shall be performed and tested in accordance with Section 15500 - "WELDING PRESSURE PIPING".

END OF SECTION

Yale University





           

Chemistry Research Building



  Prefabricated Underground Piping
Site Distribution
15600-1



    
         July 8, 2003
Yale University





           

Chemistry Research Building



  Prefabricated Underground Piping
Site Distribution
15600-6



    
         July 8, 2003

