

WM Group Engineers, P.C.

SECTION 15080

PIPING INSULATION
Part 1. GENERAL

1.1 WORK INCLUDED

A. Principal work in this Section includes labor, materials, equipment and services necessary for a complete and safe installation of mechanical piping insulation.

1.2 QUALITY ASSURANCE

A. Refer to Section 15010, GENERAL PROVISIONS - MECHANICAL.

B. Insulation materials, including jackets, facings, adhesives, coatings, and accessories, shall be fire hazard rated and listed by Underwriters' Laboratory, Inc., using the Steiner Tunnel Test Method for Fire Hazard Classification of Building Materials, Standard UL 723 (ASTM E-84) and NFPA 255.

1. The Underwriters' Laboratory, Inc. listed Class I flamespread rating shall be a maximum of 25 and the fuel contributed and smoke developed rating shall be a maximum of 50.

2. Flameproofing treatments which are subject to deterioration from moisture or humidity are not acceptable.

C. Insulation products shall carry ISO 9000/9001/9002 certification or guaranteed to meet the ISO standards.

D. Refer to Section 15010, GENERAL PROVISIONS - MECHANICAL for Guarantee and other Quality Assurance requirements.

1.3 SUBMITTALS

A. Submit product data, schedule, and samples for the following items per the provisions of Division 1 and this Division’s General Provisions:

1. Product data:  Insulation materials, vapor barrier materials, adhesives, fastening devices, and finishes and jacketing.

2. Schedule:  List the work that will be insulated and a description of insulation materials and finishing procedures and a certificate indicating compliance with codes.

3. Samples:  Insulation materials, jackets, and finishes.

1.4 DEFINITIONS

A. Exposed: Piping located in mechanical equipment rooms and in indoor areas which will be visible without removing ceilings or opening access panels.

B. Concealed:  Indoor piping which is not exposed.

C. Outdoor:  Piping which is exposed to the weather.

D. Underground:  Piping which is buried; whereas piping located in a trench below grade is considered concealed.

1.5 RELATED WORK AND REQUIREMENTS

A. Requirements of GENERAL CONDITIONS, DIVISION NO. 1 apply to all work in this Section.

1.6 REFERENCE STANDARDS

A. Published specifications standards, tests or recommended methods of trade, industry or governmental organizations apply to work in this Section.

B. Comply with all applicable national, state and local codes and refer to Section GENERAL PROVISIONS, MECHANICAL for additional Reference Standards.

Part 2. PRODUCTS

2.1 BASE BID MANUFACTURERS

A. Fiberglass insulation:

1. Certain Teed Corp.

2. Johns Manville Corp.

3. Owens-Corning Fiberglas Corp.

4. Knauf Fiber Glass.

B. Pre-molded fiberglass insulation pipe fittings:

1. Molded Acoustical Products.

2. Starr Davis.

3. ICA-Hamfab, Inc.

C. Calcium silicate insulation:

1. Johns Manville Corp.

2. Calsilite Manufacturing Corp.

3. Pabco Inc.

D. Cellular glass insulation:

1. Pittsburgh Corning Corp.

E. Finishes, adhesives and sealants:

1. Foster Products Div. of H.B. Fuller Co.

2. Hardcast, Inc.

3. Childers Products Co.

4. Armstrong World Industries.

F. Weatherproof aluminum jacket:

1. Pabco, Inc.

2. General Aluminum Supply Co.

3. Childers Products Co.

G. PVC pre-molded fitting covers (UL Class 1):

1. Johns Manville Corp. (Zecton)

2. Certain-Teed Products Corp.

3. Knauf Fiber Glass.

4. Proto Corporation.

H. Flexible uni-cellular insulation:

1. Armstrong World Industries Inc.

2. IMCOA.

3. Rubatex Corp.

I. Insulating and finishing cement:

1. Keene Corp.

2. Insulation Industries, Inc.

3. Ryder Industries, Inc.

J. Insulating tapes:

1. Compac Corp.

2. Nashua Corp.

3. Fasson.

2.2 PIPE INSULATION MATERIALS

A. Type P-1:  Molded fiberglass.  The maximum K factor shall be 0.23 at 75ºF mean temperature with a minimum density of 3 pounds per cubic foot.  Insulation shall be provided with a factory-applied all service or all purpose jacket consisting of fire retardant laminate of white kraft facing, glass scrim reinforcing and aluminum foil.  Insulation shall be similar to Johns Manville Micro-Lok AP 850.

B. Type P-2:  Molded calcium silicate.  The maximum K factor shall be 0.44 at 300ºF mean temperature with a minimum density of 15 pounds per cubic foot.  Deflection at 200 psig shall be less than 5 percent.  Insulation shall be furnished without a factory applied jacket.  Insulation shall be similar to Johns Manville Thermo-12 Gold.

C. Type P-3:  Molded fiberglass fittings.  The maximum K factor shall be 0.23 at 75ºF mean temperature with a minimum density of 4 pounds per cubic foot.  The insulation shall be similar to ICA Hamfab Molded Fittings.

D. Type P-4:  Fiberglass fitting inserts.  The maximum K factor shall be 0.23 at 75ºF mean temperature with a minimum density of 1 pound per cubic foot.  The insulation shall be similar to ICA-Hamfab 650.

E. Type P-5:  Molded cellular glass.  The maximum K factor shall be 0.42 at 75ºF mean temperature with a minimum density of 8.5 pounds per cubic foot.  Insulation shall be furnished without a factory-applied jacket.  Insulation shall be similar to Pittsburgh Corning Foamglas.

F. Type P-6:  Molded foamed plastic.  The maximum K factor shall be 0.27 at 75ºF mean temperature with a minimum density of 6 pounds per cubic foot.  The maximum permeance shall be 0.17.  Insulation shall be similar to Armstrong AP Armaflex.

G. Type P-7:  Insulating cement.  Cement shall have a rock-wool base, be asbestos free and be hydraulic setting.  Insulation shall be similar to Insulation Industries - Smooth Cote.

2.3 FINISHES, ADHESIVES, SEALANTS AND JACKETS

A. Type F-1:  Fitting covers.  Covers shall be molded white PVC jacket, UL Class 1 with a maximum permeance of 0.05.  Covers shall be similar to Johns Manville Zeston 2000 PVC.

B. Type F-2:  Vapor barrier coating.  The white vapor barrier coating shall have a 31 millimeter  dry film thickness with a maximum permeance of 0.05.  It shall be applied over 10 x 10 or 20 x 20 mesh white glass, polyester or nylon cloth reinforcing membranes.  Coating shall be similar to Foster Tite-Fit 30-35 with UL label.

C. Type F-3:  Vinyl acrylic finish.  The white vinyl acrylic breather mastic shall have a 51 mil dry film thickness.  It shall be applied over 10 x 10 or 20 x 20 mesh white glass, polyester or nylon cloth reinforcing membrane.  Mastic shall be similar to Foster GPM Mastic 35-00 with UL label.

D. Type F-4:  Aluminum jacketing.  Piping up to 4 in. shall have 0.016 in. wall thickness jacketing and piping larger than 4 in. shall have 0.020 in. wall thickness jacketing and longitudinal joints with lock seams.

Delete if not required

E. Type F-5:  Elastomeric vapor barrier mastic.  The elastomer based vapor barrier mastic shall have a 50 mil dry film thickness.  It shall be applied over 10 x 10 or 20 x 20 glass, polyester or nylon cloth reinforcing membrane.  The mastic shall be similar to Foster Monolar 60-38 or 60-56.

F. Type F-6:  White finishing and insulating cement.  One (1) coat shall be applied over hexagonal wire mesh.  Cement shall be similar to Insulation industries - Smooth Cote.

Delete if not required

G. Type F-7:  Off-white vapor seal adhesive.  Adhesive shall be non-flammable, solvent based, quick setting and with a maximum permeance of 0.05.  Adhesive shall be equal to Foster Spark-Fas 85-20.

Delete if not required

H. Type F-8:  Aluminum colored vapor barrier sealant.  The sealant shall be a fast drying solvent based elastomer equal to Foster Elastolar 95-44.

I. Type F-9:  Flexible vapor barrier sealant and bedding compound.  Compound shall be equal to Foster Foamseal 30-45.

Delete if not required

J. Type F-10:  Stainless steel jacketing.  Jacketing shall be a minimum of 0.010 inch thick.

2.4 WIRE, BANDING AND FASTENING DEVICES

A. Wire shall be a minimum 16 gauge copper clad annealed steel.  The bands shall be ¾ inch nominal width with wing seals, of minimum thickness as follows:

1. Aluminum:  0.007 inches where exposed to weather, 0.020 inches.

2. Galvanized steel:  0.005 inches.

3. Stainless steel:  0.010 inches.

B. Staples shall be the outward clinching type of corrosion resistant steel.  The weld pins which support and fasten the duct insulation shall be a minimum 1/8 inch diameter with speed washer or integral flange of minimum 1-3/8 inch diameter.  Metal lath shall consist of galvanized steel.

C. Insulation tape:  Tape shall be UL rated with all service or foil-scrim jacket to match insulation and of width as noted.  Tape shall be similar to Compac Corp. UL ASJ or UL FKJ PS Tape.

Part 3. EXECUTION

3.1 INSULATION SCHEDULE

A. Very low temperature cold piping systems:  Below 40ºF, including:

1. Low temperature water supply and return.

2. Refrigeration suction line.

3. Low temperature water treatment by-pass chemical feed.

4. Insulation schedule:

	INSULATION SCHEDULE

VERY LOW TEMPERATURE PIPING SYSTEMS BELOW 40ºF

	
	INDOOR
	OUTDOOR

	Pipe
	Type
	P-1
	P-1

	
	Finish
	-
	F-4

	Fittings And Valves
	Type 
	P-3 or P-4
	P-3

	
	Finish
	F-2 or F-1
	F-4

	Thickness
	Up to 1 inch IPS
	1 inch
	1½ inches

	
	1¼ to 4 inches IPS
	1½ inches
	2 inches

	
	Over 4 inches
	2 inches
	2½ inches

	Vapor Seal
	
	Yes
	Yes


5. Type P-6 insulation of 1 inch wall thickness may be used in lieu of type P-1.

B. Low temperature cold piping system:  40ºF to 70ºF including:

1. Chilled water supply and return.

2. Indoor condenser water supply and return.

3. Outdoor condenser water supply and return.

4. Outdoor cooling tower make-up water.

5. Boiler make-up water.

6. Water treatment by-pass chemical feed.

7. Insulation schedule: 

	INSULATION SCHEDULE

VERY LOW TEMPERATURE PIPING SYSTEMS 40ºF TO 70ºF

	
	INDOOR
	OUTDOOR

	Pipe
	Type
	P-1
	P-1

	
	Finish
	-
	F-4

	Fittings And Valves
	Type 
	P-3 or P-4
	P-3

	
	Finish
	F-2 or F-1
	F-4

	Thickness
	Up to 4 inches IPS
	1 inch
	1½ inches

	
	Over 4 inches
	1½ inches
	2 inches

	Vapor Seal
	
	Yes
	Yes


8. Type P-6 insulation of 1 inch wall thickness may be used in lieu of P-1.

C. Low temperature hot piping systems:  70ºF to 250ºF, including:

1. Low temperature hot water supply and return.

2. Emergency generator radiator jacket cooling water.

3. Heated fuel oil.

4. Low pressure steam supply to 15 psig.

5. Low pressure condensate return, except steam traps, steam trap assembly from dirt leg to shutoff valve downstream of trap, condensate cooler discharge and radiation runouts concealed in radiator enclosures.

6. Pumped condensate discharge.

7. Boiler blowdown; drain and safety valve to 8 feet above finished floor or equipment platform.

8. Insulation schedule:

	INSULATION SCHEDULE

LOW TEMPERATURE HOT PIPING SYSTEMS 70ºF TO 250ºF

	
	
	INDOOR
	OUTDOOR
	UNDERGROUND

	Pipe
	Type
	P-1
	P-1
	P-5

	
	Finish
	-
	F-4
	-

	Fittings And 
	Type 
	P-3 or P-4
	P-3
	P-5

	Valves
	Finish
	F-2 or F-1
	F-4
	-

	Thickness
	Up to 2 inch IPS
	1½ inches
	2 inches
	1½ inches

	
	2½ to 4 inches IPS
	2 inches
	3 inches
	1½ inches

	
	4 to 6 inches IPS
	2½ inches
	3½ inches
	2 inches

	
	Over 6 inches IPS
	3½ inches
	
	

	Vapor Seal
	
	No
	No
	No


D. Medium temperature hot piping system:  251ºF to 340ºF including:

1. Medium pressure steam supply, 16 to 100 psig.

2. Medium pressure steam condensate return, except steam traps.

3. Medium temperature hot water.

4. Insulation schedule:

	INSULATION SCHEDULE

MEDIUM TEMPERATURE HOT PIPING SYSTEMS 251ºF TO 340ºF

	
	INDOOR
	OUTDOOR

	Pipe
	Type
	P-1
	P-1

	
	Finish
	-
	F-4

	Fittings And Valves
	Type 
	P-3 or P-4
	P-3

	
	Finish
	F-2 or F-1
	F-4

	Thickness
	Up to 1 inch IPS
	2 inches
	2½ inches

	
	1¼ to 4 inches IPS
	3 inches
	3½ inches

	
	Over 4 inches
	3½ inches
	4 inches

	Vapor Seal
	
	No
	No


E. High temperature piping system:  341ºF to 450ºF including:

1. High pressure steam, 101 to 400 psig.

2. High pressure steam condensate return, except steam traps.

3. High temperature hot water.

4. Insulation schedule:

	INSULATION SCHEDULE

HIGH TEMPERATURE PIPING SYSTEMS 341ºF TO 450ºF

	
	INDOOR
	OUTDOOR

	Pipe
	Type
	P-1
	P-1

	
	Finish
	-
	F-4

	Fittings And Valves
	Type 
	P-2
	P-2

	
	Finish
	F-4
	F-4

	Thickness
	Up to 2 inches IPS
	2½ inches
	3 inches

	
	2½ to 4 inches IPS
	3 inches
	3½ inches

	
	Over 4 inches
	4 inches
	4½ inches

	Vapor Seal
	
	No
	No


F. Very high temperature piping system:  451ºF to 1200ºF including:

1. High pressure steam over 400 psig.

2. Indoor engine exhaust piping.

3. Insulation schedule:

	INSULATION SCHEDULE

VERY HIGH TEMPERATURE PIPING SYSTEMS 451ºF TO 1200ºF

	
	INDOOR
	OUTDOOR

	Pipe
	Type
	P-2
	P-2

	
	Finish
	F-4
	F-4

	Fittings And Valves
	Type 
	P-2
	P-2

	
	Finish
	F-4
	F-4

	Thickness
	Up to 2½ inches IPS
	3 inches
	3 inches

	
	3 to 4 inches IPS
	4 inches
	4 inches

	
	Over 4 inches
	4½ inches
	4½ inches

	Vapor Seal
	
	No
	No


G. Miscellaneous cold piping, including cooling coil drain runouts and cooling coil condensate drain lines as follows:

1. Type P-6 insulation shall be ½ inch thickness with Type P-6 (mitered) fittings and Type F-6 finish.

2. Type P-1 insulation shall be ½ inch thick.  For fittings provide Type P-3 with Type F-2 finish or Type P-4 with Type F-1 finish.

H. Non-insulated piping:

1. Gas.

2. Non-heated fuel oil.

3. Condenser water, except as noted.

4. Pneumatic control air.

3.2 INSTALLATION

A. General:

1. Apply insulation only after piping systems have passed the required pressure and leakage tests.

2. Clean piping surfaces of dust, grease and foreign matter, and dry before application of insulation.

3. Insulation shall not be installed on pipes until they have received a prime coat of paint.

4. All insulation joints shall be butted firmly together and all jackets shall be smoothly and securely installed.

5. Insulate each pipe individually.

6. Do not use multiple pieces of insulation where a full length section will fit.

7. All materials shall be installed in strict accordance with manufacturers’ recommendations.

B. Provide 2 inches minimum longitudinal jacket overlaps.  For exposed work, install overlaps toward ceiling or wall.  For weatherproof aluminum jackets, position overlaps on side to shed water.  For underground piping, place overlaps on side of pipe, turned down.  Use circumferential overlaps on weatherproof aluminum jackets.

C. Insulation passing through sleeves or other openings shall be continuous, except where firestop or firesafing materials are required.  At penetration of fire or smoke barriers, wrap pipe with rock-wool or calcium silicate insulation, seal jacket seam and seal end joints to adjacent sections of insulation.

D. Unless noted otherwise, insulation for frost-proofed piping shall be the same as specified for the particular service, except that the insulation thickness shall be two (2) times the thickness indicated and oversized to fit over pipe and heating element.  Outdoor piping shall be provided with F4 aluminum jacket.

E. Where specified, thickness of insulation exceeds available single layer thickness, install insulation in two (2) layers with joints staggered.

F. Insulate valves, bonnets, fittings, strainers, expansion joints and piping specialties.

1. For strainers, expansion joints, and accessories requiring servicing or inspection, insulation shall be removable and replaceable without damage, and enclosed within two-piece, No. 18 gauge aluminum covers fastened with cadmium-plated bolts and nuts or snap acting latches.

2. Insulation shall be of the same thickness as adjacent piping insulation.

a. In piping systems insulated with fiberglass, secure insulation with wire.  For pipes under 3 inches diameter, built-up coating of Type F-6 insulating and finishing cement to match the thickness of adjoining pipe insulation may be used.

1) Finishes, Type F-1:  Apply factory pre-molded cover and seal edges with Type F-9 vapor barrier sealer and fiberglass tape as recommended by the manufacturer.

2) Finishes, Type F-2 and F-3:  Apply uniform layer of finish coating to cover the entire surface of fitting insulation and embed layer of fiberglass tape into wet coating, extending 2 inches over adjoining pipe covering.  Apply finish layer of coating over the entire surface.

b. For above ground piping systems insulated with calcium silicate, secure pre-molded sections of calcium silicate fittings or mitered segments of pipe insulation with wires.  Under 3 inches IPS, built up coating of insulating and finishing cement to match the thickness of adjoining pipe insulation may be used, with Type F-2 finish on exposed pipes.  For exposed locations only, apply a skim coat of Type F-6 finishing cement to smooth out the surface of the fitting insulation and a coat of Type F-2 finish.

G. Insulate flanges.  Insulation sleeve shall be of the same material as the pipe insulation, to cover the flange and overlap the insulation on the adjacent piping.  For calcium silicate insulation, provide calcium silicate rings between the sleeve and the pipe insulation.

H. Outdoor locations, provide weatherproof aluminum jacket compatible with the weatherproof jacket on the adjoining pipe insulation.

I. Wiring, banding, and fastening devices:  Secure insulation to the piping in accordance with manufacturers’ recommendations.

J. At pipe hangers for fiberglass insulated piping, provide an 18 inch long calcium silicate section continuous with the adjoining pipe insulation and jacket.  Insulation protection saddles and shields shall be as specified in Section SUPPORTS AND ANCHORS.  No hangers shall be embedded in insulation.  Saddles shall be filled with insulation of type specified for the service, or filled with insulating cement.

K. Jackets and facings:  All staples shall be sealed with Type F-9 vapor barrier sealant.  Prior to sealing jackets on services below 35ºF, apply 1/16 inch minimum thickness F-9 vapor barrier coating to ends of pipe insulation at butt joints, overlapping inside surface of insulation a minimum of 2 inches.  Adhere longitudinal laps if self-sealing laps are not used and as necessary to maintain integrity of the vaporseal.  Adhere 3 inch wide joint strip, of same material as facing, at center of each butt joint, if self-sealing butt strips are not used.

1. Adhesives:  Indoor shall be Type F-9.  Weatherproof aluminum jacket shall be Type F-4.

L. Flexible uni-cellular foamed plastic insulation Type 5:  Apply insulation and fabricate fittings in accordance with the manufacturer’s installation instructions.  Use the proper size material; do not stretch or strain insulation.  Provide cork stoppers or wood inserts at supports, as recommended by the insulation manufacturer.  Where feasible, slip insulation over the pipe or tubing prior to connection and seal the butt joints with adhesive.  Where the slip-on technique is not possible, slit the insulation and apply it to the pipe.  Seal the seam and joints with contact adhesive.  Make any change from mineral fiber insulation in a straight run of pipe, not at a fitting.  Seal the joint with tape.

M. Apply adhesives and coatings in accordance with the manufacturer’s recommendations.

END OF SECTION

Company

Piping Insulation

Project Name
15080-1
8/22/2007
Company

Piping Insulation

Project Name
15080-6
8/22/2007

