

SECTION  15081



DUCTWORK INSULATION
Refer to the Construction Documents Directive for general editing procedures and for document coordination procedures.

See the Church Mechanical Directives & Guidelines for additional information regarding the work of this Section.

UPDATE  -  1 May 1996

PART 1 GENERAL
 1.1
SUMMARY
A.
Includes But Not Limited To

1.
Furnish and install thermal wrap duct insulation as described in Contract Documents.

B.
Related Work

1.
Section 15816  -  Steel Ductwork

2.
Section 15820  -  Acoustic duct liner

PART 2 PRODUCTS
 2.1
MATERIALS
A.
Thermal Wrap Duct Insulation

1.
1-1/2 inch thick fiberglass with aluminum foil scrim kraft facing and have a density of one lb/cu ft.

2.
Approved Manufacturers -

a.
Certainteed  -  Type 100 standard duct insulation

b.
Knauf  -  Duct Wrap FSK

c.
Manson  -  Alley Wrap FSK

d.
Owens-Corning  -  FRK

e.
Johns Manville  -  Microlite FSK

PART 3 EXECUTION
 3.1
INSTALLATION
In areas of high humidity, wrap exhaust ducts above the building insulation envelope with thermal insulation.  Where humidity conditions would not cause condensate problems, delete that exhaust duct insulation.

A.
Thermal Wrap Duct Insulation

1.
Install insulation as follows -

a.
On air ducts outside building insulation envelope.

b.
On outside air ducts and combustion air ducts within building insulation envelope.

c.
On other air ducts where indicated on Drawings.

2.
Do not compress insulation except in areas of structural interference.

3.
Completely seal joints.


END OF SECTION
RENOVATE BOOKSTORE/
15081-1
Ductwork Insulation

STUDENT SERVICES AREA


SUNY College at Old Westbury

SUCF Project No. 31221-808P1

