

SECTION  15143



POTABLE WATER PIPING
Refer to the Construction Documents Directive for general editing procedures and for document coordination procedures.

See the Church Mechanical Directives & Guidelines for additional information regarding the work of this Section.

UPDATE  -  4 Sep 1997

PART 1 GENERAL
Edit SUMMARY Article as necessary to give an accurate, but brief description of the work of this Section and accurate listing of related work, especially if the scope of the work is not shown graphically on the Drawings.

 1.1
SUMMARY
A.
Includes But Not Limited To

1.
Perform coring and firestopping required by work of this Section.

2.
Furnish and install potable water piping complete with necessary valves, connections, and accessories inside building and connect with outside utility lines 5 feet from building perimeter as described in Contract Documents.

B.
Related Sections

1.
Section 15055  -  General Mechanical Requirements

 1.2
REFERENCES
Delete or add references based on editing of other parts of this Section.

A.
American Society For Testing And Materials

1.
ASTM B 88-96, 'Standard Specification for Seamless Copper Water Tube'

 1.3
SUBMITTALS
A.
Quality Assurance  -  Written report of sterilization test.

PART 2 PRODUCTS
 2.1
COMPONENTS
A.
Pipe

1.
Meet requirements of ASTM B 88.

a.
Type K for underground or beneath concrete slab.  3/4 inch minimum under slabs.

b.
Type L for above ground applica​tions.

B.
Fittings  -  Wrought copper.

C.
Connections

1.
Above-Grade  -  Sweat copper type with 95/5 or 96/4 Tin-Antimony solder, Bridgit solder, or Silvabrite 100 solder.  Use only lead-free solder.

2.
Below Grade -

a.
Brazed using following type rods.

1)
Copper to Copper Connections -

a)
AWS Classification BCuP-4 Copper Phosphorus  (6 percent silver).

b)
AWS Classification BCuP-5 Copper Phosphorus  (15 percent silver).

2)
Copper to Brass or Copper to Steel Connections  -  AWS Classification BAg-5 Silver  (45 percent silver).

3)
Do not use rods containing Cadmium.

b.
Brazing Flux -

1)
Approved Manufacturers -

a)
Stay-Silv white brazing flux by J W Harris Co

b)
High quality silver solder flux by Handy & Harmon

c.
Joints under slabs acceptable only if allowed by local codes.

D.
Ball Valves

1.
Use ball valves exclusively unless otherwise specified.  Ball valves shall be by single manufacturer from approved list below.  Valves shall be two piece, full port for 150 PSI SWP.

2.
Quality Standard  -  Nibco-Scott T585 or S585

3.
Approved Manufacturers -

a.
ConBraCo 'Apollo'

b.
Hammond

c.
Honeywell-Braukmann

d.
Jenkins

e.
Milwaukee

f.
Nibco-Scott

g.
Stockham

h.
Watts

PART 3 EXECUTION
 3.1
INSTALLATION
A.
Below Grade

1.
Install piping under slabs without joints where possible.

2.
Insulate water piping buried within building perimeter.

3.
Bury water piping 6 inches minimum below bottom of slab and encase in 2 inches minimum of sand.

B.
Locate cold water lines a minimum of 6 inches from hot water line.

 3.2
FIELD QUALITY CONTROL
A.
Site Tests  -  Before pipes are covered, test systems in presence of Architect at 100 psi hydrostatic pressure for two hours and show no leaks.

 3.3
CLEANING
A.
Sterilize potable water system with solution containing 200 parts per million minimum of available chlorine and maintaining pH of 7.5 minimum.  Introduce chlorinating materials into system in manner approved by Architect.  Allow sterilization solution to remain for 24 hours and open and close valves and faucets several times during that time.

B.
After sterilization, flush solution from system with clean water until residual chlorine content is less than 0.2 parts per million.

C.
Water system will not be accepted until negative bacteriological test is made on water taken from system.  Repeat dosing as necessary until such negative test is accomplished.


END OF SECTIONADVANCE \d252
RENOVATE BOOKSTORE/
15143-1
Potable Water Piping

STUDENT SERVICES AREA


SUNY College at Old Westbury

SUCF Project No. 31221-808P1

