

SECTION  15816



STEEL DUCTWORK
Refer to the Construction Documents Directive for general editing procedures and for document coordination procedures.

See the Church Mechanical Directives & Guidelines for additional information regarding the work of this Section.

UPDATE  -  28 Oct 1997

28 Oct 97 -
Added duct sealer by Polymer Adhesive.

PART 1 GENERAL
Edit SUMMARY Article as necessary to give an accurate, but brief description of the work of this Section and accurate listing of related work, especially if the scope of the work is not shown graphically on the Drawings.

 1.1
SUMMARY
A.
Includes But Not Limited To

1.
Furnish and install above-grade ductwork and related items as described in Contract Documents.

1.2
REFERENCES
Delete or add references based on editing of other parts of this Section.

A.
American Society For Testing And Materials

1.
ASTM A 653-96, 'Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process'

 1.3
SYSTEM DESCRIPTION
A.
Design Requirements  -  Use of aluminum, or non-metallic duct is not permitted.

 1.4
QUALITY ASSURANCE
A.
Pre-Installation Meeting  -  Schedule meeting immediately before installation of ductwork.

PART 2 PRODUCTS
 2.1
COMPONENTS
A.
Square Ducts

1.
Fabricate of zinc-coated lockforming quality steel sheets meeting requirements of ASTM A 527, with G 60 coating.

Delete paragraph 2 if no ducts 36 inches and larger.  Edit paragraph a and delete paragraph b if largest ducts are over 36 inches and less than 48 inches.

2.
Duct with height or width over 36 inches shall be fabricated using SMACNA T-24 flange joints or of pre-fabricated systems as follows -

a.
Ducts with sides over 36 inches up to 48 inches  -  Transverse duct joint system by Ductmate/25, Nexus, Ward, or WDCI (Lite) (SMACNA 'E' or 'G' Type connection).

b.
Ducts 48 inches & Larger  -  Ductmate/35, Nexus, or WDCI (Heavy) (SMACNA 'J' Type connection).

c.
Approved Manufacturers -

1)
Ductmate Industries Inc, 10760 Bay Meadows Drive, Sandy, UT  84092  (801) 571-5308

Stockton, CA  (800) 344-3270

Pittsburgh, PA  (800) 245-3188

2)
Nexus, Exanno Corp, P O Box 729, Buffalo, NY  14206  (716) 849-0545

3)
Ward Industries Inc, 1661 Lebanon Church Road, Pittsburgh, PA  15236  (800) 466-9374

4)
WDCI, P O Box 10868, Pittsburg, PA  15236  (800) 248-2355

B.
Round and flat-oval duct fabrication


1.
General: Diameter as applied to flat-oval ducts in this article is the diameter of the size of round duct that has a circumference equal to the perimeter of a given size of flat-oval duct.  Duct shall be prefabricated machine formed spiral lock-seam ducts; of galvanized steel or aluminum; with matching machine formed welded seam fittings: United Sheet Metal “UNISEAL” or “UNI-RIB” ducts or acceptable equivalent by Spiromatic, Semco or U.S Air Duct.


2.
Round ducts: Fabricate supply ducts of galvanized steel according to SMACNA’s “HVAC duct construction standards – metal and flexible”.


3.
Flat oval ducts: Fabricate supply ducts with standard spiral lock seams or with butt-welded longitudinal seams according to SMACNA’s “HVAC duct construction standards - metal and flexible”.


4.
Double-wall (Insulated) ducts: Fabricate double-wall (insulated) ducts with an outer shell and an inner liner. Dimensions indicated on internally insulated ducts are inside dimensions.



a.
Thermal conductivity (K-value): 0.26 at 75 deg mean temperature.



b.
Outer shell: Base outer-shell metal thickness on actual outer-shell dimensions. Fabricate the outer-shell lengths 2 inches longer than the inner shell and insulation, and in metal thickness specified for a single-AL duct.



c.
Solid inner liner: Fabricate round and flat oval inner liners with solid sheet metal of thickness listed below.



d.
Perforated inner liner: Fabricate round and flat oval inner liners with sheet metal having 3/32 inch-diameter perforations with an overall open area of 23%. Use the following sheet metal thickness and seam construction.




1)
Ducts 3 to 8 inches in diameter:  0.019 inch with standard spiral seam construction.




2)
Ducts 9 to 42 inches in diameter: 0.019 inch with single-rib spiral seam construction.



e.
Maintain concentricity of liner to outer shell by mechanical means. Retain insulation from dislocation by mechanical means.

C.
Round and flat-oval supply fitting fabrication:


1.
90° Tees and laterals and conical tees: Fabricate to comply with SMACNA’s “HVAC duct construction standards – metal and flexible”, with metal thickness specified for longitudinal seam straight duct.


2.
Diverging-flow fittings: Fabricate with a reduced entrance to branch taps with no excess material projecting from body onto branch tap entrance


3.
Elbows: Fabricate in die-formed, gored, pleated or mitered construction. Fabricate bend radius of die-formed, gored and pleated elbows one and one-half times elbow diameter. Unless elbow construction type is indicated, fabricate elbows as follows:



a.
Mitered-elbow radius and number of pieces: Welded construction complying with SMACNA’s “HVAC duct construction standards – metal and flexible” , unless otherwise indicated.



b.
Round mitered elbows: Welded construction with the following metal thickness for pressure classes from minus 2- to plus 2-inch WG:




1)
Ducts 3 to 26 inches in diameter: 0.028 inch




2)
Ducts 27 to 36 inches in diameter: 0.034 inch




3)
Ducts 37 to 50 inches in diameter: 0.040 inch



c.
Flat-oval mitered elbows: Welded construction with same metal thickness as longitudinal seam flat oval duct.



d.
90-Degree, two-piece, mitered elbows: Use only for supply systems for material-handling classes A and B; and only where space restrictions do not permit using 1.5 bend radius elbows. Fabricate with single-thickness turning vanes.



e.
Round elbows, 8 inches or smaller: Fabricate die-formed elbows for 45- 90-degree elbows and pleated elbows for 30, 45, 60 and 90 degrees only. Fabricate non-standard bend-angle configuration or non-standard diameter elbows with gored construction.

D.
Duct Sealer

Edit the list of approved manufacturers to include only those with whom you are familiar and whose products are available in the Project area.  Do not add or approve any other manufacturers or systems without written approval of the Mechanical Group of A & E Services.

1.
Approved Manufacturers -

a.
Cain  -  Duct Butter or Butter Tak

b.
Design Polymerics  -  DP 1010

c.
DSC  -  Stretch Coat

d.
Duro Dyne  -  S2

e.
Hardcast  -  Versa Grip 102

f.
Kingco  -  15-325

g.
Mon-Eco  -  44-41

h.
Polymer Adhesive  -  Airseal #11

i.
Trans-Continental Equipment Co  -  Multipurpose Duct Sealant

j.
United  -  Water Base Duct Sealer

D.
Duct Hangers

1.
One inch by 18 gauge galvanized steel straps or steel rods as shown on Drawings, and spaced not more than 8 feet apart.  Do not use wire hangers.

2.
Attaching screws at trusses shall be 2 inch No. 10 round head wood screws.  Nails not allowed.

 2.2
FABRICATION
A.
Ducts

1.
Straight and smooth on inside with joints neatly finished.

2.
Ducts shall be large enough to accommodate inside acoustic duct liner.  Dimensions shown on Drawings are net clear inside dimensions after duct liner has been installed.

3.
Duct panels through 48 inch dimension having acoustic duct liner need not be crossbroken or beaded.  Crossbreak unlined ducts and duct panels larger than 48 inch or bead 12 inches on center.

PART 3 EXECUTION
 3.1
INSTALLATION
A.
Interface With Other Work  -  Reseal transverse joint duct leaks and seal longitudinal duct joint leaks discovered during air test & balance procedures specified in Section 13352, at no additional cost to Owner.

B.
Ducts

1.
Install internal ends of slip joints in direction of flow.  Seal transverse joints air tight using specified duct sealer.

2.
Securely anchor ducts to building structure with specified duct hangers attached with screws.  Do not hang more than one duct from a duct hanger.

3.
Brace and install ducts so they shall be free of vibration under all conditions of operation.

4.
Ducts shall not bear on top of structural members.

5.
Paint ductwork visible through registers, grilles, and diffusers flat black.

6.
Properly flash where ducts protrude above roof.

7.
Cover horizontal and longitudinal joints on exterior ducts with two layers of Hardcast tape installed with Hardcast RTA-50 adhesive according to Manufacturer's recommendations.


END OF SECTION

RENOVATE BOOKSTORE/
15816-1
Steel Ductwork

STUDENT SERVICES AREA


SUNY College at Old Westbury

SUCF Project No. 31221-808P1

