

SECTION  16138



BOXES
Refer to the Construction Documents Directive for general editing procedures and for document coordination procedures.

See the Church Electrical Directives & Guidelines for additional information regarding the work of this Section.

UPDATE  -  1 Nov 1996

PART 1 GENERAL
 1.1
SUMMARY
A.
Includes But Not Limited To

1.
Furnish and install outlet boxes as described in Contract Documents.

B.
Related Sections

1.
Section 16055  -  General Electrical Requirements

PART 2 PRODUCTS
 2.1
COMPONENTS
A.
Outlet Boxes

1.
Galvanized steel of correct size and shape.

2.
Provide metal supports and other accessories for secure installation of each box.

3.
Equip ceiling and bracket fixture boxes with fixture studs where required.

4.
Equip with extensions as required to bring box flush with finish surface.

5.
HVAC Instrumentation & Control -

a.
Junction boxes in mechanical equipment areas shall be 4 inches square.

b.
Boxes for remote sensor devices shall be recessed single device.

c.
Boxes for thermostats shall be recessed single device.

Delete Paragraph B if no floor outlets on Project.

B.
Floor Outlets

1.
Acceptable Manufacturers & Models -

a.
Walker 887 cast iron box 885 brass duplex cover plate for carpet

b.
Hubbell B-2537 cast iron box with SF3925 brass duplex cover plate for carpet

c.
Equal as approved by Architect before bidding.  See Section 01600.

PART 3 EXECUTION
 3.1
INSTALLATION
A.
Interface With Other Work

Edit or delete paragraphs 1 and 2 to fit Project circumstances.

1.
Coordinate with Division 15 for installation of exposed raceway in mechanical equipment areas.  Exact separation of responsibility is shown on Drawings.

B.
General

1.
Boxes shall be accessible and installed with approved cover.

2.
Do not locate device boxes which are on opposite sides of framed walls in the same stud space.  In other wall construction, do not install boxes back to back.

3.
Locate boxes so outlets are not obstructed by pipes, ducts, or other items.

4.
Install outlets flush with finished surface and level and plumb.

5.
Boxes for switches shall generally be located within 6 inches of door jamb.

6.
Properly center single outlets in each room.  Where two or more outlets occur, space them uniformly and in straight lines with each other.

7.
Support switch boxes larger than two-gang with side brackets and steel bar hangers in framed walls.

C.
HVAC Instrumentation & Control System

1.
Mount remote sensor outlet boxes with long dimension vertical.

2.
Mount thermostat outlet boxes with long dimension horizontal.


END OF SECTION

RENOVATE BOOKSTORE/
16138-1
Boxes

STUDENT SERVICES AREA


SUNY College at Old Westbury

SUCF Project No. 31221-808P1

