

SECTION  16410



ENCLOSED SWITCHES & CIRCUIT BREAKERS
Refer to the Construction Documents Directive for general editing procedures and for document coordination procedures.

See the Church Electrical Directives & Guidelines for additional information regarding the work of this Section.

UPDATE  -  9 Jul 1997

PART 1 GENERAL
 1.1
SUMMARY
A.
Includes But Not Limited To

1.
Furnish and install disconnects as described in Contract Documents.

B.
Related Sections

1.
Section 16055  -  General Electrical Requirements

PART 2 PRODUCTS
 2.1
EQUIPMENT
A.
Disconnects

1.
Heavy duty quick-make, quick-break type, non-fused unless indicated otherwise.

2.
Provide interlock to prevent opening of door when switch is in ON position.

3.
Provide means to lock switch in OFF position with padlock.

4.
Disconnects for motor circuits shall be horsepower rated.

Delete or edit if no furnaces on Project.

5.
Disconnects for furnace fans shall be manual starter with thermal overload relay.  Provide overload relay to match motor full load amps.

Edit paragraph 6 to show option required for Project circumstances.

6.
Enclosures -

a.
Interior  -  NEMA Type 1

b.
Exterior  -  NEMA Type 3R.

7.
Fuses -

a.
Fuse fused disconnects with dual-element time delay fuses and equip with rejection type fuse holders.

b.
Fuses on Project shall be from single manufacturer.

c.
Approved Manufacturers -

1)
Bussmann

2)
Edison

3)
GEC Alsthom/Cefco

4)
Gould/Shawmut

5)
Littelfuse

8.
Approved Manufacturers -

a.
Same as Manufacturer of Project's main panelboard.

PART 3 EXECUTION
 3.1
INSTALLATION


A.
Label disconnects to indicate equipment or panel served.  Use 1/16 inch thick laminated plastic composition material with contrasting color core.  Engraved letter shall be 1/4 inch high.  Attach labels with screws.


END OF SECTION

RENOVATE BOOKSTORE/
16410-1
Enclosed Switches & Circuit Breakers 

STUDENT SERVICES AREA


SUNY College at Old Westbury

SUCF Project No. 31221-808P1

